SECTION 031500 – CONCRETE ACCESSORIES

- GENERAL

      - SUMMARY

        - Related Documents:

          - Drawings and general provisions of the Subcontract apply to this Section.

          - Review these documents for coordination with additional requirements and information that apply to work under this Section.

        - Section Includes:

          - Anchors installed in hardened concrete, including but not limited to:

            - Expansion type anchors, including wedge-type, and shell type (drop-in) anchors.

            - Powder driven fasteners.

            - Epoxy anchors.

            - Inspection and testing of concrete anchors.

        - Related Sections:

          - Division 01 Section "General Requirements."

          - Division 01 Section "Special Procedures."

          - Division 23 Section "Supports and Anchors."

      - REFERENCES

        - General:

          - The following documents form part of the Specifications to the extent stated. Where differences exist between codes and standards, the one affording the greatest protection shall apply.

          - Unless otherwise noted, the referenced standard edition is the current one at the time of commencement of the Work.

          - Refer to Division 01 Section "General Requirements" for the list of applicable regulatory requirements.

        - International Code Council (ICC)

          - ICC	Evaluation Reports.

      - SUBMITTALS

        - Submit under provisions of Division 01 Section "General Requirements."

        - Product Data:  For each anchor type scheduled for use.  Include active ICC Evaluation Report.

      - QUALITY ASSURANCE

        - Each anchor proposed for use shall have an current ICC Evaluation report indicating allowable capacity in applicable concrete substrate materials.

      - PROJECT CONDITIONS

        - [Fill over deck is lightweight concrete.]

        - [Cast-in-place normal weight concrete.]

- PRODUCTS

      - CONCRETE ANCHORS

        - Torque-Controlled Expansion Anchors:  Kwik Bolt TZ, by Hilti (ICC ESR-1917), Strong-Bolt by Simpson (ICC ESR-1771), or approved equal.

        - Shell-type (drop-in) Anchors:  HDI by Hilti, Drop-in by Simpson, or approved equal.

        - Powder Driven Fasteners:  X-U fasteners as manufactured by Hilti, Inc.(ICC- ESR-2269), or approved equal.

        - Epoxy Adhesive (Cartridge-Type): ICC approved, two component structural epoxy; prepackaged in cartridges for manually or pneumatically operated caulk gun and automatically mixed at nozzle.  Subject to compliance with requirements provide one of the following:

- HIT RE500-SD Adhesive Anchoring System, Hilti, Inc. (ICC ESR-2322).

- HIT-HY 150 MAX-SD Adhesive Anchoring System, Hilti, Inc. (ICC ESR-3013).

- SET-XP Adhesive Anchoring Systems, Simpson Strong-Tie Co. (ICC ESR-2508).

      - ANCHOR RESTRICTIONS

        - Wedge-type Anchors:  Acceptable for applications within the limitations of the applicable ICC report.

        - Shell-type (drop-in) Anchors:  Shall not be used in applications requiring resistance to forces due to wind or earthquake or tension forces due to gravity.

        - Powder Driven Fasteners:  Shall not be used in applications requiring resistance to forces due to wind or earthquake forces or tension forces due to gravity.

        - Epoxy Anchors:  Acceptable for applications within the limitations of the applicable ICC report and shall not be used to fasten overhead, wall mounted or fire resistive construction. Epoxy dowels shall not be used for substitution of lap splices.

- EXECUTION

      - EXAMINATION

        - Examine areas to be drilled to verify conditions of access, interferences, and existing materials.

        - Locate existing reinforcing steel, which might interfere with drilling, with a suitable metal detector.

      - INSTALLATION

        - Holes for anchors and dowels shall be located to miss existing reinforcing steel wherever practical.

          - Where reinforcement is encountered and anchor cannot be shifted, install wedge type anchor with minimum 4 anchor diameter embedment above bottom of reinforcement.

        - Hole diameter shall be as specified in the applicable ICC Report for the size and type of anchor or dowel to be installed.  Hole depth shall be as necessary to obtain the embedment specified on the drawings.

          - Torque controlled mechanical anchors installed in applications to resist tension due to gravity or seismic forces shall have an embedment equal to 8 anchor diameters, wherever practical.

        - Holes shall be prepared as specified in the applicable ICC Report. At a minimum, holes shall be cleaned of all dust and debris prior to installation of anchors or dowels. Cleaning shall consist of removal of debris with oil free compressed air (90 psi (632 gr/cm²), minimum), brushing of the hole twice in a twisting motion with a nylon brush and removal of debris with oil free compressed air (90 psi (632 gr/cm²), minimum).

        - Wedge-type anchors shall be installed to the minimum torque specified in the applicable ICC Report.

      - FIELD QUALITY CONTROL

        - The Testing Laboratory will:

          - Special Inspect installation of anchors in accordance with applicable ICC Evaluation Report, where special inspection is indicated on Contract Documents or where Subcontractor's design engineer has used ICC anchor capacities that require Special Inspection.

            - Subcontractor will reimburse University for cost of Special Inspection, where anchors are sized by Subcontractor's design engineer using ICC Special Inspection values.

          - Develop and utilize an effective method of field marking anchor and dowel test locations and results.

        - Test 25 percent of torque controlled mechanical anchors installed on a given day in tension using pullout procedure.  Test to 80% of specified yield strength of the dowel or 200% of the ICC rated static capacity for 2500 psi concrete whichever is the lesser. Anchors specifically noted on the drawings as “No test required” do not require tension testing.

        - Test 25 percent of reinforcing steel dowels and threaded rods installed with epoxy on a given day in tension using pullout procedure..  Test to 80% of specified yield strength of the dowel or 150% of the ICC rated static capacity whichever is the lesser with special inspection. Dowels specifically noted on the drawings as “No test required” do not require tension testing.

        - Pull test 25 percent of epoxy-type anchors installed on a given day in tension using pullout procedure.  Test to 150 percent of the ICC rated capacity with special inspection.

        - If the failure rate of anchors or dowels exceeds 10 percent, testing will be increased to 100 percent of that day’s installation of similar anchors or dowels.  Testing will be reduced to 25 percent of that day’s installation when the failure rate is reduced to 10 percent or less.

        - Failed anchors and dowels shall be replaced at no additional cost to the University and the Subcontractor shall reimburse the University for cost of additional testing.

END OF SECTION 031500