SECTION 033053 - Miscellaneous Cast-In-Place Concrete

<Use this section for smaller projects.>

- GENERAL

      - SUMMARY

        - Related Documents:

          - Drawings and general provisions of the Subcontract apply to this Section.

          - Review these documents for coordination with additional requirements and information that apply to work under this Section.

            - Section Includes:

          - Concrete reinforcement and accessories.

        - Section Includes:

          - Concrete reinforcement and accessories.

          - Cast-in-place concrete.

        - Related Sections:

          - Division 01 Section "General Requirements."

          - Division 01 Section "Special Procedures."

      - REFERENCES

        - General:

          - The following documents form part of the Specifications to the extent stated. Where differences exist between codes and standards, the one affording the greatest protection shall apply.

          - Unless otherwise noted, the referenced standard edition is the current one at the time of commencement of the Work.

          - Refer to Division 01 Section "General Requirements" for the list of applicable regulatory requirements.

        - American Concrete Institute (ACI):

          - ACI 211.1	Proportions for Normal, Heavyweight and Mass Concrete

          - ACI 301	Specifications for Structural Concrete for Buildings

          - ACI 303.1	Specification for Cast-in-Place Architectural Concrete

          - ACI 305	Recommended Practices for Hot Weather Concreting

          - ACI 306	Recommended Practices for Cold Weather Concreting

          - ACI 308	Curing Concrete

          - ACI 309	Consolidation of Concrete

          - ACI 318	Building Code Requirements for Reinforced Concrete

        - ASTM International:

          - ASTM C31	Making and Curing Concrete Test Specimens in the Field

          - ASTM C33	Concrete Aggregates

          - ASTM C94	Ready Mix Concrete

          - ASTM C143	Test Method for Slump of Portland Cement Concrete

          - ASTM C150	Portland Cement

          - ASTM C156	Test Method for Water Retention by Concrete Curing Materials

          - ASTM C171	Sheet Materials for Curing Concrete

          - ASTM C172	Sampling of Freshly Mixed Concrete

          - ASTM C260	Air Entraining Admixtures for Concrete

          - ASTM C309	Liquid Membrane - Forming Compounds for Curing Concrete

          - ASTM C330	Lightweight Aggregates for Structural Concrete

          - ASTM C494	Chemical Admixtures for Concrete

          - ASTM C567	Test Method for Unit Weight of Structural Lightweight Concrete

          - ASTM C618	Fly Ash and Raw or Calcined Natural Pozzolan for Use as a Mineral Admixture in Portland Cement Concrete

          - ASTM C881	Epoxy - Resin - Base Bonding Systems for Concrete

          - ASTM E1745	Specification for Water Vapor Retarders Used in Contact with Soil or Granular Fill Under Concrete Slabs

        - American Association of State Highway and Transportation Officials (AASHTO):

          - M182-60 - Burlap Cloth Made for Jute or Kelat.

        - State of California, Business and Transportation Agency, Department of Transportation (Caltrans):

          - CMM Materials Manual.

          - Standard Specifications.

        - American Institute of Steel Construction (AISC) Code of Standard Practice

      - SUBMITTALS

        - Submit under provisions of Divisions 01 Section "General Requirements" and "Special Procedures."

        - Mix design for each concrete mix sealed by an engineer registered in California.

          - Include compression test data used to establish mix proportions.

        - Submit certification that all facilities of the ready-mix plant comply with the requirements of ASTM C94.

        - Material Certificates.

          - Cementitious materials, including fly ash.

          - Aggregates, including gradation and combined gradation.

          - Admixtures.  Where more than one admixture is proposed, include statement from admixture manufacturer indicating that admixtures proposed for use are compatible, such that desirable effects of each admixture will be realized.

        - Product Data:  Provide data form proprietary materials, including admixtures curing materials, and finish materials.

        - Submit ticket to Testing Laboratory for each batch of concrete delivered, bearing the following information.  Refer to "Field Quality Control" Article of this Section.

        - Mix identification.

        - Weights of cementitious materials, aggregates, water and admixtures, and aggregate size.

        - Samples:  As requested by Testing Laboratory.

        - Submit placement drawings, showing location of construction joints, if the location of construction joints will be different than shown on the construction drawings.

        - Submit test reports from the independent testing agency for review by the University.

      - QUALITY ASSURANCE

        - Quality assurance and inspection shall be in accordance with Division 01 Section "Special Procedures" .

        - Standards:  Comply with provisions of ACI 301, except where more stringent requirements are shown or specified. Evaluation and acceptance of concrete structures will be in accordance with ACI 301.

        - Concrete Mix Design:  Testing laboratory shall, under direction of its California registered Civil Engineer, design concrete mixes.  Each mix shall bear the signature, seal and registration expiration date of the engineer directing the design work.  For mixes containing greater than twenty five percent fly ash, the Testing laboratory shall produce calculations and test batches in accordance with the recommendations of ACI 211.1 to determine the minimum water content and to confirm workability, curing time and compressive strength.

        - Certificates of Compliance:  Acceptability of the following materials will be based upon documentation furnished by the manufacturer identifying each batch of material and certifying compliance with the requirements specified:

          - Portland cement.

          - Fly ash.

          - Chemical admixtures.

        - Certified laboratory test reports:  Before delivery of materials, certified copies of the reports of all tests required in referenced publications or otherwise specified here shall be submitted.  The testing shall have been performed by an independent laboratory approved by the University within one year of submittal of test reports for approval.  Test reports on a previously tested material shall be accompanied by notarized certificates from the manufacturer certifying that the previously tested material is of the same type, quality, manufacture and make as that proposed for use in this project.  Certified test reports are required for the following:

          - Portland Cement.

          - Aggregates.

          - Admixtures.

        - Survey anchor bolts for placement and alignment prior to casting concrete.

- PRODUCTS

      - FORM MATERIALS

        - Conform to ACI 301.

        - Form Ties:  Snap-off metal, cone ends.

        - Form release agent:  Non staining with no petroleum solvents; Nox-Crete Company “Nox-Crete Form Coating”, Industrial Synthetics Corporation “Synthex”, or equal.

      - REINFORCING STEEL

        - Reinforcing Steel:  ASTM A615 (unless otherwise noted on the drawings), of the yield grade specified on the drawings; deformed plain billet steel bars.

          - Recycled content shall be a minimum of 75% recycled post consumer steel.

        - Reinforcing Steel Mechanical Connectors: “Non-Slip Coupler” (standard type), manufactured by Bar Splice Products, Inc., Fox-Howlett Industries, Inc., or Lenton reinforcing steel couplers or approved equal capable of developing 125% of the specified minimum yield strength of the reinforcing steel.

      - CONCRETE MATERIALS

        - Cementitious materials and aggregates for exposed concrete shall be from same source throughout the work.

        - Cementitious Material:  An intimate blend of Portland cement and fly ash.  Cementitious material shall include 15 percent minimum to a maximum of 25% fly ash by weight unless the strength is specified to be achieved in 7 or 14 days.

          - Portland Cement: ASTM C150, Type II, low alkali.

          - Fly Ash:  ASTM C618, Class F with the following Modified ASTM requirements:

            - Loss of Ignition (L.O.I.): maximum 1%.

            - Sulfur Trioxide (SO3) shall not exceed 3% by weight.

            - Water requirement maximum:  100% control.

            - R=(CaO-5%)/(Fe2O3), where R (sulfate resistance) is 0.75 maximum and CaO/Fe2O3 is the percentage from fly ash oxide analysis.

        - Aggregate for Standard Weight Concrete:  ASTM C33, except as modified herein.

          - Coarse Aggregates:  Cleanness Value of not less than 75 when tested as per CMM-Test Method No. California 227.

          - Coarse Aggregate for Shrinkage Controlled Concrete: Lonestar or Hanson Clayton, or Sechelt, B.C. (as supplied by Hanson).

          - Fine Aggregates:  Sand Equivalent of not less than 75 when tested per CMM-Test Method No. California 217.

        - Aggregate for Lightweight Concrete:  ASTM C330.  Lightweight aggregate shall be vacuum saturated expanded shale or clay produced by rotary kiln.

        - Water:	Mixing water shall be clean, potable and free from deleterious material.

        - Admixtures:

          - General:

            - Admixtures containing more than 0.05 percent chloride ions are not permitted.

            - Where mix contains more than one admixture, all admixtures shall be supplied by one manufacturer.  Manufacturer shall certify that admixtures are compatible such that desirable effects of each admixture will be realized.

            - Liquid admixtures shall be considered part of the total water.

        - Lightweight Concrete shall contain an air entrainment admixture conforming to ASTM C260, to produce an air content of 3 to 5 percent at point of placement.

        - Water Reducing Admixture: ASTM C494, Type A.  Provide in all concrete at necessary dosage to facilitate placement.

        - Mid to High Range Water Reducing Admixture:  ASTM C494, Type F; polycarboxylate formulation.  Provide in mid-range or high-range dosage as necessary for placement at the maximum water to cement ratio specified.

        - Set Accelerating Admixture:  ASTM C494, Type E, non-chloride.  Subject to approval of University's Representative, provide in necessary dosage to accelerate set.

        - Set Retarding Admixture:  ASTM C494, Type D.  Subject to approval of University's Representative, provide in necessary dosage to retard set.

        - Color Admixtures: ASTM C579; products of Davis Colors, L. M. Scofield Co, QC Construction Products, or equal.  Provide color as approved by the University's Representative from job site samples. Exposed exterior concrete shall contain 2 pounds of lampblack per cubic yard.

      - ACCESSORIES

        - Curing Compounds:  ASTM C309, [Type I, clear or translucent without dye,] [Type 1-D, clear or translucent with fugitive dye] or Type 2, white pigmented] and which will not discolor concrete or affect bonding of other finishes applied thereover, and which restricts loss of water to not more than 0.500 grams per square centimeter of surface when tested per ASTM C156, “Test Method for Water Retention by Concrete Curing Materials.”

        - Slab Curing Membrane:  Membrane conforming to ASTM C171, non-staining.

        - Burlap Sheet:  AASHTO M182, class 3 or 4.

        - Surface Hardener:  Lapidolith, Hornolith, Kemi-Kal Liquid or equal.

        - Rock Base:  Clean, hard and durable gravel or crushed rock conforming to the requirements of CalTrans Standard Specifications Section 68 for Class 1, Type A permeable material.

        - Vapor Barrier:  ASTM D2103, “Polyethylene Film and Sheeting.”

        - Sand Cover:  Uniformly graded, clean sand free from excessive fines, organic materials or other deleterious substances.

        - Form Tie Cone Hole Plugs:  Burke Co., Grey, Recessed, Jumbo Cone, “Snaplug”, or equal (no known equal) with waterproof adhesive.

        - Filter drains such as behind concrete walls:  Type A drain rock conforming to Division 31 Section "Backfilling" or prefabricated drain manufactured with polyethylene stranded or molded core and a geotextile fabric bonded to one side.  Filter drains shall be manufactured by Mirafi, Exxon or equal approved by the Architect-Engineer.

        - Embedded Reglets and Dovetail Anchor Slots:  18 gauge galvanized steel.

        - [Bonding Agent: Burke Acrylic Bondcrete, Thorobond or equal.]

      - CONCRETE MIXES

        - Schedule of Concrete Classes:

| Mix ID/Use | Aggregate Size (inches) | Slump (inches) | Min. Strength (psi) | Other Req'ts |
| --- | --- | --- | --- | --- |
| Mix A Drilled Piers, Foundations | Size 57 (1") | 4 to 6 | 4000 |  |
| Mix B Walls, Columns, Suspended Slabs & Beams | Size 57 (1") | 4 to 6 | 4000 | Req't E.1, Req't E.2 |
| Mix C Floor Slabs on Grade, Miscellaneous Concrete | Size 57 (1") | 3-5 | 4,000 | Req't E.1, Req't E.2 |
| Mix D Lightweight Concrete Fill on Metal Decking | 1/2" x #4 lightweight | 3-5 | 4,000 | Req'ts E.2 and E.3 |
| Mix E Miscellaneous concrete for curbs, pads, etc. | Size 57 (1") | 3-5 | 3,500 |  |
| Lean Concrete | Size 57 (1") | 3 to 5 | 1,500 |  |

        - Aggregate:  Coarse aggregate size number in accordance with ASTM C33 for normal-weight aggregate.  Coarse aggregate size in accordance with ASTM C330 for lightweight aggregates.

        - Slump:  Minimum-maximum slump at point of placement in inches when tested in accordance with ASTM C143.

        - Strength:  Minimum compressive strength in psi after [7] [14] [28] days, tested in accordance with ASTM C39.

        - Other Requirements (apply only where indicated in Schedule of Concrete Mixes)

          - Shrinkage Controlled Concrete:  Use special coarse aggregates specified.  Select materials and proportion mix to achieve shrinkage less than 0.040% (ASTM C157 modified).

          - Water to Cementitious Material Ratio:  Mixes "B","C" and "D" shall have a water-to-cementitious-material ratio not exceeding 0.45 by weight.  Weight of water shall include all free moisture, including liquid admixtures.  Mixes shall contain specified high range water reducing admixture at mid-range dosage as required to achieve specified slump.

          - Lightweight Concrete:  Equilibrium weight (at 100 days air dry) of 113 pcf plus or minus 3 pcf, ASTM C567.  Mix shall contain 4 percent, plus or minus 1 percent, entrained air by volume at point of placement.

        - Proposed mixes shall produce concrete to strengths specified with adequate workability and proper consistency to permit concrete to be worked into forms and around reinforcement without excessive segregation or bleeding.

        - Mix design shall be subject to review by the University's Representative and the Testing Laboratory.  Mixes shall be submitted in ample time for review and adjustment, if necessary.

        - Add air entraining agent to normal weight concrete mix for work exposed to exterior.

        - For concrete exposed to special exposure conditions the maximum water-cement ratio shall not exceed [0.5].

- EXECUTION

      - EXAMINATION

        - Verify site conditions under provisions of Division 01 Section "General Requirements".

        - Verify requirements for concrete cover over reinforcement.

        - Verify that anchor bolts, embedded plates, reinforcement, sleeves and other items to be cast into concrete are accurately placed, positioned securely, and will not cause hardship in placing concrete.

      - FORMWORK ERECTION

        - Verify lines, levels, and measurement before proceeding with formwork.

        - Hand trim sides and bottom of earth forms; remove loose dirt.

        - Align form joints.

        - Do not apply form release agent to concrete surfaces which receive [special finishes] [or] [applied coatings] that may be affected by agent.

        - Coordinate work of other sections in forming and setting openings, slots, recesses, chases, sleeves, bolts, anchors, and other inserts.

      - REINFORCEMENT  & EMBEDDED ITEMS

        - Place, support, and secure reinforcement and embedded items  against displacement.

        - Installation tolerances for anchor bolts for structural steel columns shall comply with the AISC Code of Standard Practice tolerances.

        - Only items that are dimensionally located on the drawings may be embedded in concrete regardless of the trade responsible for placing them.

      - PLACING CONCRETE

        - Notify the University at least 48 hours prior to commencement of concreting operations.  No concrete shall be placed until all subgrade, formwork, reinforcing steel, embedded items and surfaces against which concrete is to be placed have been accepted by the University.  The rate of delivery, haul time, missing time and hopper capacity shall be such that all mixed concrete delivered shall be placed in forms within 90 minutes from the time of the introduction of cement and water into the mixer.  No water shall be added after transit mixer leaves the batching plant without the approval of the University.

        - Prepare previously placed concrete by cleaning with [steel brush] or [sandblasting] [waterblasting] [wet sandblasting] and applying bonding agent in accordance with manufacturer’s instruction.

        - In locations where new concrete is doweled to existing work, drill holes in existing concrete, insert steel dowels and pack solid with [non-shrink grout] or [epoxy grout].

        - Foundation surfaces against which concrete is to be placed must be free from standing water, mud and debris.  Surfaces shall be clean and free from oil, objectionable coatings, and loose or unsound material.

        - All surfaces of forms and embedded items shall be free of grout before placing concrete.

        - Install [joint fillers] and [waterstops] in accordance with manufacturer’s instructions.  Install [1/2-inch] thick joint filler to separate slabs on grade from vertical surfaces.  Extend joint filler from bottom of slab to within ¼-inch of finished slab surface.

        - Location of construction joints shall be as shown on the structural drawings.

        - When ambient temperature is expected to exceed 80F during placing or finishing operations, steps shall be taken in accordance with ACI 305, “Recommended Practices for Hot Weather Concreting”, to reduce concrete temperature and water evaporation by proper attention to the ingredients, production methods, handling, placing, protection and curing. The Subcontractor shall submit a detailed hot weather concrteting procedure to the A/E for approval at least two business days before concrete placement is planned. The Subcontractor’s testing agency will produce trial batches in accordance with ACI 305. Slabs will be fog sprayed from the completion of skreeding until curing is begun; the fog spray may be discontinued on sections during troweling.

      - FLOOR SLABS

        - Place floor slabs [in long strip patterns] [as indicated on Drawings]. Saw cut control joints at an optimum time after finishing.  Cut slabs with a 3/16-inch thick blade to 1 inch depth.

        - Separate slabs on grade from vertical surfaces with joint filler.  Extend joint filler from bottom of slab to within ¼ inch of finished slab surface.

        - [Scratch] [Float] [Trowel] [Broom or belt] [Nonslip] finish surfaces [as scheduled].

        - Install joint devices and joint device anchors in accordance with manufacturer’s instructions.  Maintain correct position to allow joint cover flush with floor finish.

        - Construct slab on grade and shored elevated floor slabs with overall specified FF30/FL20 and with minimum FF15/FL10 for individual floor sections in accordance with ACI 302.1. Determination of FF/FL numbers will be in accordance with ASTM E 1155. The Subcontractor will take remedial measures when floor slabs do not meet specified requirements The Subcontractor’s plan for remedial measures shall be submitted to the University for review and approval.  [Pitch slabs to drains [1/4] [     ] inch per foot nominal.]

      - [SCHEDULE OF FORMED SURFACES

        - Smooth surface finish at [                        ].

        - Rough form finish at [                              ].

        - Smooth form finish at [                            ].

        - Smooth rubbed finish at [                         ].

        - Cement slurry finish at [                           ].]

      - [SCHEDULE OF FLOOR SLAB FINISHES

        - Scratch finish at [                                                                 ].

        - Float finish at [                                                                     ].

        - Trowel finish at [                                                                  ].

        - Broom or belt finish at [                                                       ].

        - Nonslip finish at [                                                                 ].]

      - CURING AND PROTECTION

        - The requirements of this section may be modified only by the Structural Engineer of Record (SER) for the design. In those cases where the Structural Engineer of record is under subcontract to the Laboratory, approval by a Laboratory Structural Engineer is required prior to modification of the requirements of this section.

        - Wheeling, working and walking on concrete shall be avoided for at least 24 hours after casting.  Protect concrete from sun and rain.  Do not permit concrete to become dry during curing period.  Concrete shall not be subjected to any loads until concrete is completely cured, and until concrete has attained its 28 day strength and [14 days minimum] [28 days minimum].

        - Protect concrete during and after curing from damage during subsequent building construction operations.

        - Cover traffic areas with plywood or other suitable means for as long as necessary to protect concrete from damage.

        - Specific curing requirements for slabs shall include the following: Immediately upon completion of finishing operation, the surface of slabs shall be sealed against moisture loss by the application of a curing blanket made of polyetheylene bonded to burlap in accordance with the manufacturer’s instructions. Alternatively, waterproof curing paper may be used with edges lapped and sealed with tape. The curing membrane shall be weighted down.  Tears and rips in curing membrane shall be repaired immediately during curing period.  Curing shall be maintained for [7] [14] [21] days.

        - Specific curing requirements for walls, beams and columns shall include the following:  Concrete in forms shall be kept moist until removal.  Immediately upon removal of forms, an approved sprayed-on curing compound shall be applied to the concrete surfaces in strict compliance with the manufacturer’s recommendations.  Curing shall be maintained for [7] [14] days.

        - For above grade concrete sections over three feet thick except lean concrete:

          - Ten days before placing concrete, the results of thermal test performed by the Subcontractor will be submitted to the University for approval.  Thermal tests shall consist of a three foot test cube of the design mix for the thick section instrumented with thermocouples by the Subcontractor’s testing agency and monitored to determine whether the heat of hydration exceeds 150°F.  If the temperature exceeds 150°F, the mix design will be revised or standard aggregate cooling utilized and a second test cube cast and tested at no additional cost to the University.

          - The temperature gradient between the center and the surface of the section must not exceed 20°F during the first ten days of the controlled curing period.  Thermocouples shall be installed by the Subcontractor’s testing agency in the center and six inches from the surface at twenty foot intervals and at the corners.  The thermocouples are to be monitored continuously by the Subcontractor’s testing agency and, if the temperature gradient exceeds 20°F, insulating blankets shall be placed over the surface.  On surfaces with protruding reinforcing, such as the top of a wall, loose insulation will be used.

      - FIELD QUALITY CONTROL

        - Inspection and Testing will be performed under provisions of Division 1.

        - Testing Laboratory will:

          - Collect and review tickets for each batch of concrete delivered.  Annotate water or admixtures added subsequent to batching.

          - Special Inspect concrete placement, as required by CBC Section 1701.5, Item 1, for conformance with the Contract Documents.

          - Slump:  ASTM C143; one test at point of placement at start of each day's pour; additional tests when concrete consistency appears to have changed.

          - Compressive Strength:  Test concrete for compressive strength in accordance with CBC Section 1905.6 and ASTM C39.  Conform to testing frequency of CBC 1905.6.1.  Take 4 specimens per sample, test one at seven days, two at 28 days, and retain one specimen.

          - Temperature:  ASTM C1064; one test hourly.  Take additional tests where warranted by weather conditions or delays in delivery.

          - Air Content:  ASTM C173; for mixes with more than 3 percent air, take one test hourly at point of placement.

        - The Subcontractor shall pay Testing Laboratory for investigating of low-strength compressive test results in accordance with CBC Section 1905.6.4.

END OF SECTION 033053