SECTION 220111.13 – TESTING AND MAINTENANCE OF PLUMBING

- GENERAL

      - SUMMARY

        - Related Documents:

          - Drawings and general provisions of the Subcontract apply to this Section.

          - Review these documents for coordination with additional requirements and information that apply to work under this Section.

        - Section Includes:

          - Cleaning and flushing building piping systems.

          - Testing building piping systems.

          - Disinfecting building piping systems.

          - Placing building piping systems in operation.

        - Related Sections:

          - Division 01 Section "General Requirements."

          - Division 01 Section "Special Procedures."

          - Division 22 Section "Identification for Plumbing Piping and Equipment".

          - Division 22 Section "Facility Plumbing Piping".

          - Division 23 Section "Hydronic Piping".

          - Division 23 Section "Steam and Condensate Heating Piping".

          - Division 23 Section "Refrigerant Piping".

          - Division 33 Section "Operation and Maintenance of Utilities".

      - REFERENCES

        - General:

          - The following documents form part of the Specifications to the extent stated. Where differences exist between codes and standards, the one affording the greatest protection shall apply.

          - Unless otherwise noted, the referenced standard edition is the current one at the time of commencement of the Work.

          - Refer to Division 01 Section "General Requirements" for the list of applicable regulatory requirements.

          - Refer to Division 22 Section "Common Results for Plumbing" for codes and standards, and other general requirements.

        - Code of Federal Regulations (CFR):

          - 29 CFR 1910  Occupational Safety and Health Standards (OSHA)

        - American Water Works Association (AWWA):

          - AWWA C601  Disinfecting Water Mains

        - Compressed Gas Association (CGA):

          - CGA G4.1  Cleaning Equipment for Oxygen Service

        - Factory Mutual Engineering (FM):

          - FM  Factory Mutual System Loss Prevention Data Sheets

        - International Association of Plumbing and Mechanical Officials (IAPMO):

          - IAPMO UPC  Uniform Plumbing Code

        - National Fire Protection Association (NFPA):

          - NFPA-12A  	Halon 1301 Fire Extinguishing Systems

          - NFPA 13  	Installation of Sprinkler Systems

          - NFPA 14  	Installation of Standpipe and Hose Systems

          - NFPA 15  	Water Spray Fixed Systems for Fire Protection

          - NFPA 20  	Installation of Centrifugal Fire Pumps

          - NFPA 30  	Flammable and Combustible Liquids Code

          - NFPA 31  	Installation of Oil Burning Equipment

          - NFPA 51  	Design and Installation of Oxygen-Fuel Gas Systems for Welding, Cutting and Allied Processes

          - NFPA 51B  	Fire Prevention in Use of Cutting and Welding Processes

          - NFPA 54  	National Fuel Gas Code

      - ABBREVIATIONS

        - CA	=	Compressed Air

        - CHW	=	Chilled Water

        - DCW	=	Domestic Cold Water

        - DHW	=	Domestic Hot Water

        - DIW	=	Deionized Water

        - fps	=	Feet per Second

        - HWW	=	Healing Hot Water

        - ICW	=	Industrial Cold Water

        - IHW	=	Industrial Hot Water

        - MAWP	=	Maximum Allowable Working Pressure

        - MPG	=	Natural Gas (Medium Pressure)

        - N	=	Nitrogen Gas

        - NG	=	Natural Gas (Low Pressure)

        - LCW	=	Low Conductivity Water

        - TRW	=	Treated Water

        - TW	=	Tower Water

        - VAC	=	Vacuum

      - SUBMITTALS

        - Submit under provisions of Division 22 Section "Common Results for Plumbing, Review of Materials" and Division 01 Section "General Requirements."

        - Submit testing, cleaning, and disinfecting procedures.

      - PROJECT CONDITIONS

        - Water to be discharged from flushing and disinfecting procedures shall be neutralized and disposed of in accordance with Division 01 Section "Special Procedures" or Division 33, Section 33110.

- PRODUCTS	NOT USED

- EXECUTION

      - CLEANING AND FLUSHING

        - Water Piping Systems:

- <Water piping systems included in this subpart are CW, LCW, DW, steam, steam condensate, chilled water, heating hot water, building domestic hot and cold water, building drainage, and vent piping systems.  Edit to provide only the specific information needed for the project.  Cross-out any piping system and all sizes and velocities that are not part of this job.>

          - After completion of all work in each section of the various water piping systems, and prior to testing, flush all piping to remove foreign material and to thoroughly clean the system.  Flushing shall be continued until the water leaving the system is clear and acceptable to the University, but in no case shall the flushing be performed for less than 10 minutes.

          - Ensure that adequate quantities of water are available to produce a flushing velocity of not less than 2.5 fps (0.8 m/s).

          - Use DIW for flushing DIW piping.  Use DCW to flush DCW, DHW, IHW, ICW, CHW, TW TRW, HHW and all other piping systems.

          - See Section 22 "Facility Plumbing Piping", for special cleaning requirements of DIW piping.

        - Gaseous Piping Systems:

- <Gaseous piping systems included in this subpart are CA, natural gas, house vacuum,   nitrogen gas,  oxygen gas, carbon dioxide gas, and refrigerant piping systems.  Edit to provide only the specific information needed for the project.>

          - After completion of all work in each section of the piping system, but prior to testing, blow the piping clean with oil-free compressed air or nitrogen to the satisfaction of the University.

          - Select paragraph below for particularly critical installations or as clients demand.

          - Perform an inert gas purge with sample analysis using gas chromatography to ensure no unacceptable level of contaminants exist inside the piping system.

          - Oxygen Piping:

            - Give special consideration for oxygen piping.  Before installation, thoroughly clean all piping, valves, fittings, and other components of oil, grease, and other readily oxidizable materials by washing in a hot alkaline cleaner-water solution, such as sodium carbonate or trisodium phosphate (proportion of 1 lb/3 gal or 1 kg/25 L water).  Scrub where necessary to ensure complete cleaning.  After washing, thoroughly rinse the materials in clean, hot water, and hot-air dry prior to capping or protective plugging.  After cleaning, exercise particular care in storing and handling such materials.

            - Temporarily cap or plug the cleaned components to prevent recontamination before final assembly.

            - Just prior to final assembly, examine each component internally for contamination, and reclean if necessary.

          - Deliver piping, valves, fittings, and other components that have been especially prepared and cleaned in accordance with the provisions of CGA G-4.1 and capped or plugged.  Reinspect prior to final assembly, and reclean if necessary.

          - During assembly do not use any oils or lubricants that are incompatible with oxygen.  If recontamination during piping assembly is suspected, reclean the entire piping system.  If required by the University, perform an inert-gas purge with sample analysis using gas chromatography.

      - PRESSURE TESTING PIPING SYSTEMS

        - General:

          - Prior to acceptance and initial operation, inspect and test the piping systems to ensure that the design, materials, fabrication, and installation are in accordance with these specifications.

          - Test piping prior to being enclosed, covered-up, or treated externally with insulation, tape wrapping, mastic coating, and like treatments.

          - Notify the University at least 48 hours prior to testing, and conduct tests in the presence of a University Representative.

          - Piping systems shall show no pressure loss, unless noted otherwise, while being tested in accordance with this section of these specifications.  When leakage or other defects are located, repair or replace the affected portion of the piping system and retest.  In the event repairs, replacement, or additions are made following the pressure test, retest the affected piping.  In the case of very minor repairs, replacement, or additions, the University may, solely at its discretion, omit retesting provided precautionary measures are taken to assure sound construction.

        - General Test Procedures:

          - All valves shall be in full-open position during the test.  Do not include any components (gauges, relief valves, instrumentation, and like items) as part of the tests that are not rated for the testing pressure.

          - Do not attempt to modify a piping system when it is pressurized, including tightening leaking joints.  Do not repair, replace, or retighten leaking joints or components until the pressure has been reduced to ambient level.

          - Measure test pressure with a manometer or with a pressure-measuring device designed and calibrated to read, record, or indicate the maximum test pressure.  Record any pressure loss due to leakage during the pressure test period while the system is pressurized but isolated from the pressure source.

          - In general, test nonhazardous liquid, inert gas, and compressed air system at a minimum of 125% of their MAWP, and test toxic, oxygen, radioactive, and flammable fluid systems at a minimum of 150% of their MAWP using an inert fluid.  The test pressure for each piping system shall be not less than the following values, irrespective of the design MAWP:

| TEST SYSTEM | TEST PRESSURE (Gauge) | TES MEDIA | TEST DURATION |
| --- | --- | --- | --- |
| DCW, ICW, DHW, IHW, CHW, TW, TRW, HHW, LCW | 225 psi gauge (1553 kPa) | ICW | 24 hours |
| DIW | 150 psi gauge (1035 kPa) | DIW | 24 hours |
| CA, VAC | 150 psi gauge (1035 kPa) | CA (oil free) | 4 hours |
| Natural Gas, N2 | 165 psi gauge (1139 kPa) | Nitrogen Gas | 4 hours |

          - Prepare test records of inspection and all tests performed.  Indicate which portions of the piping system are in accordance these specifications.  Briefly document test procedures, instruments and media used, and test pressures.  Before requesting final approval of a piping installation, submit copies of test records for University approval.

      - SPECIAL REQUIREMENTS

        - Special Procedures for Gas Piping:

          - Test duration shall be a minimum of 4 hours.

          - The piping system shall withstand the test pressure specified without showing any evidence of leakage or other defect.  Any reduction of test pressures as indicated by pressure gauges shall be deemed to indicate the presence of a leak unless such reduction can be readily attributed to some other cause.

          - Locate the leakage using a University-approved combustible gas detector, soap and water, or an equivalent nonflammable solution as applicable.  Do not use open flames or other methods which could provide a source of ignition.

          - After completion of the pressure test and before turning gas under pressure into new systems, check to ensure that all openings from which gas can escape are closed.

          - Purge the inert gas with fuel gas in accordance with NFPA 54, section 4.3 before placing the pipeline in service.

        - Special Procedures for Building Drainage and Vent Piping:

          - Water test the building drainage and vent piping system either in its entirety or in sections.

          - If the water test is applied to the entire system, tightly close all openings (except the highest opening) in the system to the end of the building sewer at its points of connection with the site sewage system, and fill the piping system with water.

          - If the system is tested in sections, test every section with a minimum pressure of 10 ft-water-column (30 kPa).  In testing successive sections, test at least the upper 10 feet (3 m) of the next preceding section so that no joints or pipe in the building except the uppermost 10 feet (3 m) of the system are submitted to a test pressure of less than 10 ft-water-column (30 kPa).  Keep the water in the system, or portion under test, for at least 24 hours before starting inspection.  The system shall be watertight at all points.

        - Special Procedures for Building Domestic Hot and Cold Water Supply Piping:  Upon completion of a section or of the entire system, water test the section or system and prove tight under a pressure not less than 125% of its MAWP or 125 psi (1 550 kPa) gauge, whichever is greater, for a period of 24 hours.

        - Special Procedures for Refrigerant Piping:

          - Test the refrigerant piping system for 24 hours at 300 psi (2070 kPa) gauge for the high side and 150 psi (1035 kPa) gauge for the low side.

          - Do not use oxygen for acetylene to test refrigerant piping; use nitrogen only

      - DISINFECTING CW/HW PIPING SYSTEM

        - General:  Clean and disinfect all cold water systems in accordance with AWWA C601 when the project is complete and when, by test, the system is proven to be free from leaks and ready for use.  Subcontractor shall contract with Bennett Marine Utility Inc, 1027 California Drive, Burlingame, CA 94010-3630.  Phone 650-344-0436.

        - Disinfecting Procedure:

          - Connect the injection hose to the test connection.

          - With the system completely full of water and the supply valve open, proceed to adjust every valve of the system so that a trickle of water flows from each.

          - Inject the disinfectant slowly, at a uniform rate, until an orthotolidine test at each outlet shows a minimum chlorine residual concentration of 100 parts per million (ppm).

          - Close all outlets and valves, including the valve connecting to the water-supply line and the 3/4-inch (19-mm) service cock on the solution-injection connection.

          - Maintain the condition for 24 hours.  If after 24 hours, orthotolidine tests indicate that the chlorine residual concentration has decreased below 50 ppm, repeat the disinfecting procedure until an approved result is obtained.

          - When the residual chlorine requirements have been fulfilled, the part of the water system being disinfected shall be drained and flushed until the chlorine concentration of the discharged water has been reduced to an amount equivalent to the level normally present in the water supplied to the area.  This part of the system shall again be isolated by valving off.  All drainage and flushing water shall be directed to the sanitary sewer system.

          - After checking that the residual chlorine concentration is not greater than control levels using the orthotolidine test, the Contractor shall take water samples after a 24 hour incubation period at predetermined locations of the isolated system.  The sampling points shall be chosen so as to provide accurate information regarding the bacteriological quality of the water.  The samples shall be analyzed by Bennett Marine Utility Inc, 1027 California Drive, Burlingame, CA  94010-3630 Phone 650-344-0439.  Before putting this system into service, the results of these tests must show the water to completely free (i.e., <1 or none detected) from coliform organisms after a 24 hour incubation period.

          - If the results of the bacteriological tests do not meet the standard specified above, the disinfection procedures shall be repeated until this standard is satisfied.

          - Tie-in fittings to be placed in existing mains shall be sterilized either by immersing in a chlorine solution of 500 ppm for one-half hour or by swabbing with fire (5) percent hypochlorite solution.

          - On system where a fire sprinkler riser is to be directly connected to an existing underground link that has been previously sterilized and terminates above ground, the double check valves, test cocks, and all pipe and fittings between the check valves and the termination of the underground line, are to be immersed in a 500 ppm chlorine solution for one (1) hour prior to assembly.  The termination of the underground line is not be left uncovered any longer than necessary.  The sterilization process is to be monitored by LBNL EH&S Division or his representation and a University Inspector.

          - Bennett Marine Utility Inc. shall issue a Certification Sterilization / Chlorination to the subcontractor to demonstrate satisfactory completion of the above procedure.  The subcontractor shall submit the Certification to LBNL for their review.

        - Disinfecting Agent:  The Subcontractor will supply the disinfecting agent and the injecting apparatus, will inject the disinfecting agent into the system, and operate the valves.

        - Preparation:

          - Provide a test connection for the system to be disinfected within 2-3 feet (0.6-0.9 m) of its junction with the water supply lines, for injecting the disinfectant into the system.

          - Prepare the water-flow valves for sterilization.

          - Thoroughly flush the system by fully opening every outlet and operating every fixture until clear water flows from all of them.

      - DISINFECTING LCW or DI PIPING SYSTEM

        - Low Conductivity Water (LCW) or Deionized (DI) Water:  After water system piping is installed and pressure tested, flush pipe with trisodium phosphate to remove any dirt, oil, and grease.  After flushing, pump 3% hydrogen peroxide at 20 psig (138 Kpa), to flush clean.  Rinse system with low conductivity water or deionized water after sterilization until all traces of chlorine are gone.  Notify the LBL Project Manager 10 days prior to rinsing the system.  It is the Contractor's responsibility to clean the piping system of all debris and visible contaminants.  It is absolutely essential that the pipe system is free of any oil, grease, or other contaminants.  Perform all of the above in the presence of the LBNL Project Manager or his representative.

      - PLACING IN OPERATION

        - After approval of tests and flushing and cleaning operations, place the systems in operation.

END OF SECTION 220111.13