SECTION 221519.13 – GENERAL SERVICE PACKAGED RECIPROCATING AIR COMPRESSORS

- GENERAL

      - SUMMARY

        - Related Documents:

          - Drawings and general provisions of the Subcontract apply to this Section.

          - Review these documents for coordination with additional requirements and information that apply to work under this Section.

        - Section Includes:

          - Reciprocating air compressor.

          - Air receiver and accessories.

          - After cooler.

          - Refrigerated air dryer or Desiccant air dryer.

          - Pressure-reducing station.

          - Critical sir filtration system or general purpose coalescing or microfiltration final filters.

          - Oil-water separator

          - Drain Valves.

        - Related Sections:

          - Division 01 Section "General Requirements."

          - Division 01 Section "Special Procedures."

          - Division 23 Section "Direct Digital Control System for HVAC".

      - REFERENCES

        - General:

          - The following documents form part of the Specifications to the extent stated. Where differences exist between codes and standards, the one affording the greatest protection shall apply.

          - Unless otherwise noted, the referenced standard edition is the current one at the time of commencement of the Work.

          - Refer to Division 01 Section "General Requirements" for the list of applicable regulatory requirements.

          - Refer to Division 22 Section "Common Results for Plumbing" for codes and standards, and other general requirements.

        - American Society for Testing and Materials (ASTM) - ASME BPVC Boiler and Pressure Vessel Code Section VIII Pressure Vessels

      - ABREVIATIONS

        - CFM – Cubic Feet per Minute

        - PSI – Pounds per Square Inch

        - PSIG – Pounds per Square Inch Gage

      - SUBMITTALS

        - Submit under provisions of Division 22 Section "Common Results for Plumbing, Review of Materials" and Division 01 Section "General Requirements."

        - Submit inspector's certificate for Air Receiver with Operating and Maintenance Manuals

      - QUALITY ASSURANCE

        - Air receivers shall meet requirements of ASME BPVC, Section VIII, and shall carry ASME approval stamp.

- PRODUCTS

      - ACCEPTABLE MANUFACTURERS

        - Ingersoll Rand, Devilbiss, Joy or Hitachi.

        - No Substitutions

      - TYPE

        - Provide duplex compressor unit consisting of oil-free air-cooled motor-compressor, air receiver, aftercooler, [refrigerated air dryer or desiccant air dryer,] [pressure-reducing station,] spring isolators, and operating controls.

      - PERFORMANCE

        - Compressors shall operate at specified air volume without oil creep, overloading, and within 10% of peak efficiency.

        - Each compressor shall continuously deliver [	    ] [as scheduled] cfm ([    ] m³/minute) of free air at intake conditions compressed to [	  ] psi ([  ] kPa) at 800 feet (245 m) altitude, when driven by [	]-hp electric motor.

        - The water-cooled after cooler shall have the capacity to cool [	] cfm ([    ] m³/minute) at [        ] psi ([  ] kPa) .

        - Refrigerated air or desiccant air dryer shall have capacity to dry air to an atmospheric dew point of [   ] deg F ([  ] deg C) at the rated air flow of [	] cfm ([    ] m³/minute) at [	]-psig ([  ] kPa) inlet air pressure.  The pressure differential from inlet to outlet shall not exceed [       ] psi ([  ] kPa) .

        - Provide [	]-[inch (mm)] [foot (m)] diameter by [	]-[inch (mm)] [foot (m)] long, [   ] gallon (lt) capacity] air receiver.

      - COMPRESSOR CONSTRUCTION

        - The compressor unit shall be constructed with cast iron housing and head, heat-treated forged steel or ductile iron shaft, aluminum alloy connecting rods, aluminum pistons with [non-lubricated carbon] rings, and high-strength alloy suction and discharge valves.  Rotating parts shall be statically and dynamically balanced.

        - Equip compressor with an oil-pressure switch to shut-down compressor automatically in the event of oil-pressure failure.

        - Provide compressor with automatic capacity-reduction equipment consisting of suction-valve unloaders and lifting mechanism operated by [oil pressure] [gas-discharge pressure] [solenoid valve] [centrifugal force].  Provide for unloaded compressor start.

        - Mount motor and compressor on one-piece, ribbed, cast iron or welded steel base with provision for V-belt adjustment.

<Optional>

        - [Provide thermostatically controlled water valve on compressor to work in conjunction with the control circuit to maintain water temperature through the compressor within the range of 98 to 109 deg F (36.6 to 42.7 deg C).]

      - AFTERCOOLER

        - Provide the air compressor with an air aftercooler suitable for 135-psig (931.5 kPa) working-pressure operation.

        - The aftercooler shall be constructed with removable tube nests of nonferrous metal tubes and corrosion-resistant tube plates, safety valves, pressure gauge, moisture separator, moisture drain valve, water-inlet piping with automatic water valve, automatic condensate trap and overflow piping with open funnel.

        - The aftercooler capacity shall cool discharge air to within 12 deg F (11.1 deg C) of ambient air temperature when compressor is operating at specified capacity.

      - AIR DRYER

        - Provide a refrigerated air dryer of a self-contained mechanical-refrigeration type, complete with heat exchanger, refrigeration compressor, automatic controls, moisture removal trap, internal wiring and piping, and full refrigerant charge.

        - Air inlet and air outlet connections will be at the same height, and factory insulated.

        - Heat exchangers shall consist of air-to-air and refrigerant-to-air coils.  Provide centrifugal-type moisture separator located at discharge of the heat exchanger.  Provide heat exchangers with automatic control system to bypass refrigeration system on low-load or no-load condition.

        - Refrigeration unit of the hermetically sealed type shall operate continuously to maintain the specified 21 deg F (6.11 deg C) dew point.  The unit will be housed in a steel cabinet, provided with an access door and panel for maintenance and inspection.

        - Dryer shall be provided with air-inlet temperature gauge, air-inlet pressure gauge, "ON/OFF" switch, high-temperature light, "POWER ON" light, refrigerant gauge, air-outlet temperature gauge, and air-outlet pressure gauge.  The dryer shall be provided with controller with auxiliary summary alarm contacts for remote summary alarm monitoring by the Facilities Monitoring and Control System.

      - AIR RECEIVER

        - Provide ASME rated air receiver 200 PSI rated, carbon steel construction; Roy E. Hanson, Southgate Engineering, or equal.  Air receiver shall have flange or screw inlet and outlet connections.

        - Fittings shall include adjustable pressure regulator, safety valve, pressure gauge, drain cock, and automatic condensate trap.

        - Tank finish:  Shop primed.

      - PRESSURE-REDUCING VALVE

        - Provide pressure-reducing stations complete with automatic reducing valve and bypass, and low-pressure-side relief valve and gauge.  [Provide oil separator where indicated.]

        - Valve capacity, suitable to reduce pressure from 200 psi to 30-psi, shall be adjustable upwards from reduced pressure.

      - CONTROLS

        - Pressure switch shall cut-out at 100 psi with differential of at least 20 psi.

        - For compressor pairs, regulation shall be through a lead-lag switch with a time-delay relay.

        - For compressor pairs provide electrical alternation set to operate each compressor for 12 hours. In the event one compressor fails, the other compressor shall automatically maintain air pressure.

        - Control panel shall include fused disconnect, circuit breaker, magnetic starter, and H-O-A-switch.  Circuitry shall include transformer for control circuits, green pump-on lights, amber power-on light, red transformer failure light.  Circuit board shall include dry contacts for remote summary alarm monitoring by the facilities Monitoring and Control System.  Control panel shall be NEMA 12 enclosure.

      - Filters

        - For critical air system such as clean rooms:  Critical air filtration system capable of removing 99.95% of oil and water aerosols down to 0.1 microns and oil carryover of 0.5 ppmw, 359 cfm (10.2 m³/minute) at 150 psig (1035 kPa); Flair “Mist eliminator” model ME-250, Sentry, or equal.

        - General purpose:  model D-0175-CC general purpose coalescing, model D-0175-CF high efficiency coalescing, model D-0170-PF particulate filter, model D-0170-PF particulate filter; Deltech, or equal.

        - Microfilttration Final Filter:  Model MT1N-0110 microfilttration final filter rated at 0.01 micron, PTFE polypropylene membrane elements; Parker Filtgration, or equal.

        - Moisture separator filter system consisting of two filter stages, 10 micron separation and 3 micron filter, grade 9; Hankinson model HF-1-28-8-DGL, or equal.

        - Oil-water separator for treating discharge from filters, relief valves: Beko Owamat 2, or equal

      - Drain Valves

        - Automatic electronic drain valves for removal of condensate from receivers; Flair, or equal, Model NCD24, max 120 psi compressed air, 250 psi operating pressure.

- EXECUTION

      - INSTALLATION

        - Install compressor unit on a concrete foundation with a sole plate and isolators.  Level, grout, and bolt in place.

        - Provide an air cock and drain connection on the horizontal casing.

        - Install full bore ball valve and anti-return valve on the compressor discharge.

        - Install replaceable cartridge-type filter silencer of adequate capacity for each compressor.

        - Place shut-off valve on the water inlet to the aftercooler.  Pipe the drain to floor drain.

        - Pipe condensate drains to nearest floor drain.

        - Install valved bypass around air dryer.  Factory-insulate the inlet and outlet connections of the dryer.

        - Install valved drip connections at low points of piping system.

        - Install branches to outlets from the top of the main line, with a shut-off valve after the branch take-off.

        - Install compressed air couplings, 3/8-inch (9.5 mm) female speed couplers, and pressure gauges where outlets are indicated.

        - Install tee pieces in lieu of elbows at changes in the direction of piping.  Fit open end of each tee with plug.

END OF SECTION 221519.13