SECTION 260501 – inspections and testing for Electrical work

- GENERAL

      - SUMMARY

        - Related Documents:

          - Drawings and general provisions of the Subcontract apply to this Section.

          - Review these documents for coordination with additional requirements and information that apply to work under this Section.

        - Section Includes:

          - The Subcontractor shall furnish services, skilled and common labor, and apparatus and materials required for testing each phase or portion of work and/or the completed work as shown and within the intent of the Drawings and these Specifications and various LBNL safety procedures and programs as well as all other appropriate, industry standard, manufacturer recommended or code required inspections and tests.

          - Electrical testing requirements are found in various sections in Division 01 and in Division 26.  It is not the intent of this Section to duplicate efforts or to require the Subcontractor to perform any inspection or test twice.  Inspections and tests by the Subcontractor are expected to occur once in the normal installation sequence, exclusive of checks and tests required in the commissioning process.  Identical electrical inspection and testing requirements in both Division 01 and Division 26 are usually referring to the same event.

          - Continuous special inspection:  The [Subcontractor] [University] shall provide continuous full-time observation of installation and/or testing of work requiring inspection by an approved electrical inspector who shall be present in the area where work is being performed.

          - Periodic special inspection:  The [Subcontractor] [University] shall provide intermittent or part-time observation of installation and/or testing of work requiring inspection by an approved electrical inspector who shall be present in the area where work has been or is being performed and at the completion work.

          - Testing and electrical inspection includes, but is not limited to, the work outlined in Part 3 of this Section and shall be performed in addition to and in accordance with all other requirements of the Drawings and Specifications.

        - Related Sections:

          - Division 01, Section 010000, General Requirements.

          - Division 01, Section 013500, Special Procedures.

          - Division 01, Section 019113, General Commissioning Requirements.

          - This Section applies to all other Division 26 Sections.

      - REFERENCES

        - General:

          - The following documents form part of the Specifications to the extent stated.  Where differences exist between codes and standards, the one affording the greatest protection shall apply.

          - Unless otherwise noted, the edition of the referenced code or standard that is current at the time of the “date of record” for the Work shall be considered the effective code or standard for the duration of the project.

          - Refer to Division 01, Section 010000, General Requirements, for the list of applicable regulatory requirements.

          - Refer to specific Division 26 Sections for additional referenced codes and standards.

        - ANSI/NFPA 70 - National Electrical Code.

        - ANSI - American National Standards Institute.

        - Illuminating Engineering Society of North America (IES).

        - LBNL Construction Details and Design Guidelines (CDDG), Vol. 3 – Construction Details, Part VI – Electrical Details.

        - LBNL Electrical Authority Having Jurisdiction:  Standard Procedure for Safe Electrical Installations (IAHJ Program).

        - LBNL Electrical Safety Manual.

        - LBNL Facilities Department Lateral Force Design Criteria.

        - LBNL Pub-3000 Chapter 8 – Electrical Safety Program.

        - LBNL Pub-3000 Chapter 14 – Electrical Equipment Safety Program.

        - LBNL Pub-3000 Chapter 18 – Lockout/Tagout Program.

        - National Electrical Safety Code (NESC).

        - NFPA – National Fire Protection Association:  Standard for Electrical Safety in the Workplace (NFPA 70E).

        - NETA ATS - Acceptance Testing Specifications for Electrical Power Distribution Equipment and Systems.

- [Add additional Codes, Standards and Regulations that may be required for Inspection and Testing Work that are not listed in other Division 26 Sections]

      - SUBMITTALS

        - Submit for the University’s review and approval and prior to commencing work testing procedures, testing methods, certificates of calibration of test apparatus to be used and sample test reports that will be employed in performing tests and inspections required by this and other Division 26 Sections.

        - Daily Inspection and Test Reports:  Inspectors shall keep records of inspections and tests and shall furnish daily inspection reports to the Project Manager and/or his representative and the LBNL Utility Group Electrical Engineer.  Reports shall indicate that the work inspected was or was not completed in accordance with the Drawings and Specifications.  Discrepancies shall be brought to the immediate attention of the Project Manager, LBNL Utility Group Electrical Engineer and the Registered Design Professional (RDP) prior to the completion of that phase of work or the acceptance of completed work.

        - Final Inspections and Test Reports:  Final reports documenting the required inspections, tests and corrections of any discrepancies noted in previous inspections and tests shall be submitted as required by the specific Section and/or to validate that the completion of that phase of work or the acceptance of completed work is in accordance with the Drawings and Specifications.

      - quality assurance

        - Inspections:  Refer to Division 01, Section 013500, Special Procedures, “Inspections”.

        - Quality Control:  Refer to Division 01, Section 013500, Special Procedures, “Quality Control”.

        - If the Drawings or Specifications do not appear clear or definitive, the Subcontractor shall request the Project Manager through ‘Request for Information’ (RFI) process for an interpretation and decision of same, and shall have such questions decided before proceeding with the Work.

        - Qualifications and Certification Requirements:

          - Electrical inspectors shall hold current Inspector Certification with the International Code Council or equivalent organization recognized by the University.  Evidence of certification shall be submitted sixty (60) calendar days prior to scheduling of work for review and approval by the University.  The Electrical Inspector shall not be associated with the manufacturer of equipment or systems under inspection and/or test.

          - The Certified Inspecting Company (CIC) performing the work of this section shall be qualified to inspect and test electrical equipment and is a NETA (National Electrical Testing Association)-certified testing agency.  Evidence of certification shall be submitted sixty (60) calendar days prior to scheduling of work for review and approval by the University.  The CIC shall not be associated with the manufacturer of equipment or systems under inspection and/or test.

          - Test Equipment:  The Subcontractor shall provide all test equipment necessary to fulfill the checks and testing requirements.  Electrical equipment testing instruments must be calibrated in accordance with the following frequency:

            - Field Instruments:  Analog, 6 months maximum, digital, 12 months maximum.

            - Laboratory Instruments:  12 months.

            - Leased specialty equipment:  12 months where accuracy is guaranteed by lessor.

            - Torque wrench:  12 months.

        - Refer to Division 01, Section 019113, General Commissioning Requirements, for additional requirements.

- [Additional qualification and certification requirements for Inspectors and Inspection/Testing companies]

        - Standardized inspection and test forms:  The CIC shall submit three (3) copies of standardized inspection and test forms that will be used.

      - COORDINATION

        - Refer to Division 01, Section 010000, General Requirements, “Coordination of Work”.

        - Refer to Division 01, Section 013500, Special Procedures, “Coordination”; and Section 013500A, Supplement for Equipment Energization Plan: Energization Validation & Authorization Package (EVAP).

        - Refer to the LBNL Electrical Authority Having Jurisdiction:  Standard Procedure for Safe Electrical Installations (IAHJ Program) in regards to the Facilities Energization Validation and Authorization Package (EVAP) process necessary before equipment energization.

- PRODUCTS	NOT USED

- EXECUTION

      - general

        - Upon completion of the electrical construction work, perform tests and provide test reports as specified in this and other Division 26 Sections.

        - Tests shall be made in the presence of an LBNL Inspector or the Electrical AHJ’s designated representative.  The application or interruption of power shall be directed by the Responsible Individual (RI) in accordance with the approved EVAP, inclusive of the Equipment Energization Plan and Method of Procedure (MOP).

        - Immediately upon completion of testing and inspection the Subcontractor shall submit to the Project Manager five (5) copies of the field test results, certified in writing, witnessed, signed and dated by the testing technician, the Electrical Inspector and the LBNL inspector or Project Manager’s designated representative.

        - Unsatisfactory conditions, discrepancies, missed items, etc., revealed by the inspections and/or test results or the implementation of unsatisfactory methods of testing and/or testing apparatus and instruments shall be corrected by the Subcontractor to the satisfaction of the Project Manager and the RDP.  Unsatisfactory conditions, testing methods or testing equipment shall be corrected by the Subcontractor [immediately] [within __ calendar days] [within a time period agreed upon in writing].  Once corrective measures have taken place, all pertinent and required tests and inspections shall be repeated and reported as called out above.

        - The Project Manager reserves the right to require that the Subcontractor perform and repeat tests that are deemed necessary to complete or confirm the tests or the certified records of the Subcontractor at any time during the course of the work.

        - The Subcontractor shall submit final test and inspection reports within [thirty (30)] [__] calendar days of the satisfactory testing and/or inspection of the work signed by the CIC engineering representative.

        - After inspection and test reports have been reviewed and approved by the University, approval to energize will be given in accordance with the approved Equipment Energization Plan and EVAP.  Refer to the listed Section, subsection, or paragraph for inspection and testing requirements.

      - INSPECTIONS AND TESTS

          - Testing and electrical inspection includes, but is not limited to, the work required by the following outlined sections and subsections, including validating equipment and material is NRTL labeled/listed.

        - Section 260513 Medium Voltage Cable

          - 1.4.E.  Factory inspection and witness testing

          - 2.2.K.  Conductor and shield continuity tests

          - 3.3.  Test laboratory requirements

          - 3.4.  15kV Cable testing immediately after installation

          - 3.5.  15kV Cable testing after splicing and end termination preparation

          - 3.6.  15kV Voltage, phase rotation and phase sequence tests

        - Section 260519.11 600 Volt Conductors and Cable

          - 3.4.  Inspection and Tests

            - 3.4.B.  Inspections, including equipment safety grounds and bonding to the grounding system.

            - 3.4.C.  Insulation tests

            - 3.4.D.  Ground grid tests

            - 3.4.E.  Torque test all terminations

            - 3.5.B.  Voltage, phase rotation and phase sequence tests

        - Section 260519.12 Metal Clad Cable

          - 3.5.  Inspection and Tests

            - 3.5.C.  Fitting tightness and continuity tests

            - 3.5.D.  Insulation tests

            - 3.5.E.  Torque tests

            - 3.6.B.  Voltage, phase rotation and phase sequence tests

        - Section 260523 Low Voltage Electrical Power Conductors and Cables

          - 3.1.  Inspection and Verification

          - 3.5.  Testing

            - 3.5.B.1.  Conductor insulation and continuity tests

            - 3.5.B.2.  Shield continuity tests

            - 3.6.B.  Tests after energization/activation of conductors

        - Section 260526 Secondary Grounding for Electrical Systems

          - 3.2.  Field Quality Control

            - 3.2.B.  Inspect grounding and bonding of system conductors, bonding to equipment, torque tests.

            - 3.2.C. and 3.2.D.  Fall of Potential test

        - Section 260573 Electrical System Studies

          - 2.5.  Protective Device Testing, Adjustment and Modification

        - Section 260800 Commissioning of Electrical Systems

          - Part 4 – Equipment Specific Verification and Testing Requirements

            - 4.2.  Checks and Tests

            - 4.3.C.  Common Testing Requirements

            - 4.3.D.  Equipment Specific  Testing Requirements

              - 4.3.D.1.  Scheduled Lighting Controls

              - 4.3.D.2.  Occupancy Sensor Lighting Controls

            - 4.3.E.  Test Methods

              - 4.3.E.2.  Emergency Generator System

              - 4.3.E.3.  Step Load Tests

              - 4.3.E.4.  Uninterruptible Power Supply

              - 4.3.E.5.  Fire Alarm

        - Section 260923 Lighting Control Devices

          - 3.4.  Field Services and Test

          - 3.5.  Demonstration and Acceptance

        - Section 261116 Secondary Unit Substations

          - 3.1.  Factory Tests

            - 3.1.A.  Test Requirements

            - 3.1.B.  Design Tests

            - 3.1.C.  Production Tests

            - 3.1.D.  Inspection (University witness testing and inspection)

          - 3.3.  Field Quality Control

            - 3.3.A.  Inspection and testing by manufacturer’s field technician

            - 3.3.C.  Incoming Section, Transformer and LV Section tests, including torque tests.

          - 3.4.  Transformer tap settings

          - 3.5.  Acceptance and Energization

        - Section 261213 Liquid-Filled medium Voltage Transformers

          - 3.3.  Field Quality Control

            - 3.3.B.1.  Visual and mechanical inspection, including torque test.

            - 3.3.B.2.  Dielectric and electrical testing

          - 3.4.  Transformer tap settings

          - 3.5.  Acceptance and Energization

        - Section 261300 Medium Voltage Outdoor Metal Clad Switchgear

          - 2.25.  Factory Tests

            - 2.25.A.  Test Requirements

            - 2.25.B.  Design Tests

            - 2.25.C.  Production Tests

            - 2.25.D.  Inspection (University witness testing and inspection)

          - 3.1.  Field Quality Control

            - 3.1.D.1..  Vendor inspection, calibration, testing, including torque tests, and startup

            - 3.1.D.2.  Functional tests

          - 3.2.  Acceptance and Energization

        - Section 261323 SF6 Gas Insulated Switches

          - 3.1.  Factory Production Tests

          - 3.2.  Field Quality Control

            - 3.2.A.  Witness testing

            - 3.2.B.  Visual and mechanical inspection and testing, including torque tests, by Vendor

        - Section 262213 Low Voltage Distribution Transformers

          - 3.2.  Inspection and Tests

            - 3.2.B.  Insulation and other testing

            - 3.2.C.  Visual and mechanical inspection, including torque tests.

            - 3.3.B.  Voltage, phase rotation and phase sequence tests; tap settings

        - Section 262416 Panelboards

          - 3.2.  Field Quality Control

            - 3.2.A.  Witness testing

            - 3.2.B.  Visual and mechanical inspection, including torque tests

            - 3.2.C.  Insulation testing

            - 3.3.B.  Voltage, phase rotation and phase sequence tests.

            - 3.3.C.  Balanced load testing

        - Section 262419 Motor Control Center

          - 3.2.  Field Quality Control

            - 3.2.A.  Witness testing

            - 3.2.B.  Inspection, testing, calibration and start-up by manufacturer’s technician

            - 3.2.C.  Visual and mechanical inspection, including torque tests

            - 3.2.D.  Insulation tests

            - 3.2.E.  Continuity tests

            - 3.2.F.  Operational tests

            - 3.2.G.  Verify protective devices

          - 3.3.  Acceptance and Energization

            - 3.3.B.  Voltage, phase rotation and phase sequence tests

        - Section 262423 Enclosed Low Voltage Motor Controllers

          - 3.2.  Inspection and Tests

            - 3.2.A.  Witness testing

            - 3.2.B.  Visual and mechanical inspection, including torque tests

            - 3.2.C.  Insulation and continuity testing

            - 3.2.D.  Operational tests

            - 3.2.E.  Verify overcurrent protective devices

          - 3.3.B.  Voltage, phase rotation and phase sequence tests

        - Section 262600 Power Distribution Units (PDU’s)

          - 3.2.A.  Witness inspection, testing and start-up by factory trained field-service personnel.

          - 3.3.  Acceptance and Energization

        - Section 262713 Electricity Metering

          - 3.2.  Field Quality Control

            - 3.2.A.  Witness testing

            - 3.2.B.  Visual and mechanical inspection.

            - 3.2.C.  Insulation and continuity testing of wiring.

          - 3.3.  Acceptance and Energization

            - 3.3.B.  Check meter operating properly.

        - Section 262726 Wiring Devices

          - 3.3.  Field Quality Control

            - 3.3.D.  Testing of 120-volt convenience receptacles

            - 3.3.E.  Testing of GFCI receptacles

            - 3.3.F.  Testing of other than 120-volt convenience receptacles

        - Section 262816 Enclosed Low Voltage Circuit Breakers

          - 3.2.  Field Quality Control

            - 3.2.A.  Witness testing; inspection, testing, calibration and start-up by manufacturer’s technician

            - 3.2.C.  Visual and mechanical inspection, including torque tests

            - 3.2.D.  Insulation testing

          - 3.3.  Acceptance and Energization

            - 3.3.B.  Voltage, phase rotation and phase sequence tests

        - Section 262816.11 Safety Disconnect Switches

          - 3.2.  Field Quality Control

            - 3.2.A.  Witness testing; inspection, testing, calibration and start-up by manufacturer’s technician

            - 3.2.C.  Visual and mechanical inspection, including torque tests

            - 3.2.D.  Insulation testing

          - 3.3.  Acceptance and Energization

            - 3.3.B.  Voltage, phase rotation and phase sequence tests

        - Section 262923 Variable Frequency Drives

          - 3.4.  Field Quality Control

            - 3.4.A.  Witness testing

            - 3.4.B.1.  Visual and mechanical inspection, including torque tests

            - 3.4.B.2. & 3.4.B.3.  Insulation tests

          - 3.5.  Acceptance and Energization

            - 3.5.B.  Subcontractor acceptance testing per manufacturer’s instructions and University’s supervision

            - 3.5.C.  Voltage, phase rotation and phase sequence tests

        - Section 263213 Packaged Engine Generator

          - 3.1.  Factory Prototype Tests

          - 3.2.  Factory Production Tests (University witness testing at the factory)

          - 3.4.  Job Site Testing (load testing per NFPA 110 Chapter 5-13) by the manufacturer’s technician

        - Section 263213.11 Engine-Generator Load Test Bank

          - 3.1.  Field Quality Control

            - 3.1.A.  University witnessing field testing.

            - 3.1.B.  Vendor and/or subcontractor field testing; testing to be performed in conjunction with engine-generator testing.

        - Section 263213.13 Mobile Engine Generator

          - 3.1.  Factory Prototype Tests

          - 3.2.  Factory Production Tests (University witness testing at the factory)

          - 3.3.  Job Site Testing (load testing per NFPA 110 Chapter 5-13) by the manufacturer’s technician

        - Section 263313 Batteries and Battery Chargers

          - 3.2.  Field Testing and Commissioning

          - 3.3.  Acceptance and energization

        - Section 263323 Central Battery Inverter Equipment

          - 3.1.  Factory Testing (University witness testing at the factory)

          - 3.3.  Field Testing and Commissioning

          - 3.4.  Acceptance and energization

        - Section 263353 Static Uninterruptible Power Supply

          - 3.1.  Factory Testing (University witness testing at the factory)

          - 3.3.  Field Testing and Commissioning – Witness inspection, testing and start-up by factory trained field-service personnel.

          - 3.4.  Acceptance and energization

        - Section 263533 Automatic Power Factor Correction Capacitor Bank

          - 2.5.  Factory Tests

            - 2.5.A.  Test requirements and University witness testing at the factory.

            - 2.5.B.  Design Tests

            - 2.5.C.  Production Tests

            - 2.5.D.  Field testing and commissioning by manufacturer’s representative.

          - 3.3.  Field Quality Control

            - 3.3.A.  Witness testing.

            - 3.3.E.  Site Tests

          - 3.4.  Acceptance and energization.

        - Section 263623 Automatic Transfer Switch With Bypass-Isolation Feature

          - 3.1.E.  Commissioning in conjunction with the engine-generator per NFPA 110 Chapter 5-13

          - 3.3.  Field Quality Control

            - 3.3.A.  Witness inspection, testing and start-up by factory trained field-service personnel.

            - 3.3.F.  Testing with the standby/emergency generator as a system.

            - 3.3.G. and H.  Full load testing in all positions and modes of operation.

          - 3.4.  Acceptance and energization.

        - Section 264200 Cathodic Protection

          - 3.7.  Field Quality Control

            - 3.7.A.  University required inspection prior to backfilling

            - 3.7.E.  Weld strength testing (hammer blow test)

            - 3.7.F.  Dielectric strength test

            - 3.7.G.  Bolt and flange resistance test

          - 3.8.  Acceptance and energization

        - Section 265000 Lighting

          - 3.8.  Field Quality Control

            - 3.8.B.  Operational tests

            - 3.8.C. and 3.8.D.  Illumination level tests

- [Add Scope and Scheduling Requirements of Specific Special Inspection and Testing Work as needed.]

END OF SECTION 260501