SECTION 260533.11 – SURFACE raceways for electrical systems

- GENERAL

      - SUMMARY

        - Related Documents:

          - Drawings and general provisions of the Subcontract apply to this Section.

          - Review these documents for coordination with additional requirements and information that apply to work under this Section.

        - Section Includes:

          - Surface Raceway.

        - Related Sections:

          - Division 01, Section 010000, General Requirements.

          - Division 01, Section 013500, Special Procedures.

          - Division 07, Section 078413, Penetration Firestopping.

          - Division 26, Section 260500, Common Work Results for Electrical.

          - Division 26, Section 260501, Inspections and Testing for Electrical Work.

          - Division 26, Section 260533, Electrical Conduit.

          - Division 26, Section 260533.13, Boxes for Electrical Systems.

      - REFERENCES

        - General:

          - The following documents form part of the Specifications to the extent stated.  Where differences exist between codes and standards, the one affording the greatest protection shall apply.

          - Unless otherwise noted, the edition of the referenced code or standard that is current at the time of the “date of record” for the Work shall be considered the effective code or standard for the duration of the project.

          - Refer to Division 01, Section 010000, General Requirements, for the list of applicable regulatory requirements.

          - Refer to specific Division 26 Sections for additional referenced codes and standards.

        - ANSI/NFPA 70 - National Electrical Code.

        - ANSI - American National Standards Institute.

        - LBNL Construction Details and Design Guidelines (CDDG), Vol. 3 – Construction Details, Part VI – Electrical Details.

        - LBNL Electrical Authority having Jurisdiction: Standard Procedure for Safe Electrical Installations (IAHJ Program).

        - LBNL Electrical Safety Manual.

        - LBNL Facilities Department Lateral Force Design Criteria.

        - LBNL Pub-3000 Chapter 8 - Electrical Safety Program.

        - LBNL Pub-3000 Chapter 14 – Electrical Equipment Safety Program.

        - LBNL Pub-3000 Chapter 18 - Lockout/Tagout Program.

        - NFPA – National Fire Protection Association:

          - Standard for Electrical Safety in the Workplace (NFPA 70E).

      - SUBMITTALS

        - Submit under provisions of Division 01, Section 010000, General Requirements, “Submittals”; Division 01, Section 013500, Special Procedures, “Drawings and Specifications”; Division 26, Section 260500, Common Work Results for Electrical, “Submittals"; and as required by other sections of the Specifications."

        - Shop Drawings:  The Subcontractor shall submit for approval Shop Drawings prepared in accordance with Division 01, Section 010000, General Requirements, “Submittals”; and as required by other sections of the Specifications.

        - All submittals and shop drawings shall be reviewed and approved by the LBNL Utility Group Electrical Engineer before procurement or fabrication of material and equipment.

        - Submit Shop Drawings and Product Data for surface raceway system components to be used.  Clearly identify the specific products and material intended to be used.

      - QUALITY ASSURANCE

        - Products shall be tested, approved and labeled/listed by Underwriters Laboratories, Inc., or by a nationally recognized testing laboratory (NRTL) as listed in Division 26, Section 260500, Common Work Results for Electrical.

        - Electrical equipment and materials shall be new and within one year of manufacture, complying with the latest codes and standards.  No used, re-built, refurbished and/or re-manufactured electrical equipment and materials shall be furnished on this project.

      - DELIVERY, STORAGE, AND HANDLING

        - Deliver materials to site in unopened cartons or bundles as appropriate, clearly identified with manufacturer's name, Underwriter's Label, grade or identifying number.

        - Store in a clean, dry space.  Maintain factory wrapping or provide an additional heavy canvas or heavy plastic cover to equipment and material from dirt, water, construction debris, and traffic.

- PRODUCTS

      - SURFACE RACEWAY

        - Acceptable Manufacturer's

          - Panduit, Wiremold, or equal.

          - Substitutions:  Comply with Division 01, Section 010000, General Requirements.

        - Surface raceway shall be a two-piece (channel and cover) system fabricated of No. 14 gauge minimum thickness solid steel and shall be supplied complete with elbows, device cover plates and necessary fittings.  The surface raceway shall have a gray baked enamel finish that can be over-painted to suit required finish color.

        - Surface raceway used for combined power and communications shall have a divider plate installed.

- EXECUTION

      - INSTALLATION

        - Except for vertical routing to source or termination points, surface-metal raceways shall be used only where allowed by NFPA 70.  Surface-metal raceways passing from one floor to another shall have mechanical protection to a height of 4 feet (1.2 m) above the floor level.

        - Install surface raceway in accordance with manufacturer's instructions.

        - Support raceway on 8-foot (2.4 m) centers (maximum), at bends, and tee fittings.

        - Connect sections of raceway together with edges free from burrs and sharp projections.

        - Except where specifically noted, all field joints shall he made with non-bolted quick-fastening devices that will not diminish the strength or electrical ground continuity of the raceway assembly.

        - Surface raceway shall use manufacturer's wire clip spaced at a maximum of three feet to hold conductors in place.

        - Permanently and effectively ground surface raceway systems in accordance with Division 26, Section 260526, Secondary Grounding for Electrical Systems.

END OF SECTION 260533.11