SECTION 260800 - Commissioning of Electrical Systems

- GENERAL

      - SUMMARY

        - Related Documents:

          - Drawings and general provisions of the Subcontract apply to this Section.

          - Review these documents for coordination with additional requirements and information that apply to work under this Section.

        - Section Includes:

          - This section specifies the unique responsibilities that are a part of, or are related to the commissioning process for the electrical systems.  Electrical systems include those listed in Division 01, Section 019113, General Commissioning Requirements, as being commissioned.  All statements are the responsibility of the Subcontractor, unless specifically stated otherwise.

          - Electrical testing specified for systems not listed as formally commissioned are not under the commissioning umbrella and are not governed by this section.

          - Electrical Systems Commissioning consists of static checks of component and system installations and actual testing of equipment conditions and functions.

          - The Commissioning Authority or University shall review and approve, prior to use, all test procedures and forms used and shall witness a varying fraction of the initial checks and testing performed by the Subcontractor.  The Commissioning Authority shall review the completed check and test documentation of the Subcontractor of all checks and tests.

          - Electrical testing requirements are found in various sections in Division 01 and in Division 26 (Division 01, Section 019113, General Commissioning Requirements; Division 26, Section 260501, Inspections and Testing for Electrical Work; and this Section).  It is not the intent of the commissioning process or these specifications to duplicate efforts or to require the Subcontractor to perform any check or test twice.  Checks and testing by the Subcontractor are expected to occur once in the normal sequence of installation and checkout, if appropriate coordination has occurred allowing the University and the Commissioning Authority to witness installations and initial testing.  Identical electrical checks and testing requirements in both Division 01 and Division 26 are referring to the same event.

          - The test requirements listed in this section do not release the Subcontractor from the obligation to perform all other appropriate, industry standard, manufacturer-recommended or code-required checks and tests.

          - Testing Participants.  The work of this section shall be performed by parties identified in “Check and Testing Responsibility Table”, Supplement 3 to Division 01, Section 019113, General Commissioning Requirements.  Static checks and testing shall be fully documented according to provisions in Division 01, Section 019113, General Commissioning Requirements.

        - Related Sections:

          - Division 01, Section 010000, General Requirements.

          - Division 01, Section 013500, Special Procedures.

          - Division 01, Section 019113, General Commissioning Requirements.

          - Division 01, Section 260501, Inspections and Testing for Electrical Work.

          - This section applies to all other Division 26 Sections.

      - SUBMITTALS

        - Submit under provisions of Division 01, Section 010000, General Requirements; and Section 013500, Special Procedures.

        - Submit for the University’s review and approval and prior to commencing work testing procedures, testing methods, certificates of calibration of test apparatus to be used, and sample test reports that shall be employed in performing tests and inspections required by this and other Division 26 Sections.

      - QUALITY ASSURANCE

        - Qualifications:

          - The CTC (Certified Testing Company) performing the work of this section shall be qualified to test electrical equipment and is a NETA (National Electrical Testing Association)-certified testing agency.  The CTC shall not be associated with the manufacturer of equipment or systems under test.

        - Test Equipment:

          - The Subcontractor shall provide all test equipment necessary to fulfill the checks and testing requirements.  Test equipment shall be calibrated in accordance with the following frequency:

            - Field Instruments:  Analog: 6 months maximum; digital: 12 months maximum.

            - Laboratory Instruments:  12 months.

            - Leased specialty equipment:  12 months where accuracy is guaranteed by lessor.

          - Refer to Division 01, Section 019113, General Commissioning Requirements, for additional requirements.

      - COORDINATION

        - Refer to Division 01, Section 010000, General Requirements, “Coordination of Work”.

        - Refer to Division 01, Section 013500, Special Procedures, “Shutdown”; and Section 013500A, Supplement for Equipment Energization Plan: Energization Validation & Authorization Package (EVAP).

        - Refer to the LBNL Electrical Authority Having Jurisdiction: Standard Procedure for Safe Electrical Installations (IAHJ Program) in regards to the Facilities Energization Validation and Authorization Package (EVAP) process necessary before equipment energization.

- PRODUCTS	NOT USED

- EXECUTION

      - SUBMITTALS

        - Sixty (60) days before any testing is conducted, submit an overall testing plan and schedule for electrical systems that lists the equipment, modes to be tested, dates of testing and parties conducting the tests.  Put these tests into the master construction schedule.  Keep this plan and schedule updated.

        - Additional submittal requirements relative to commissioning are found in this Section and in Division 01, Section 019113, General Commissioning Requirements; and Division 01, Section 010000, General Requirements.

      - COMMON RESPONSIBILITIES

        - The following are responsibilities applicable to all electrical systems being commissioned.

        - The general commissioning requirements and coordination are detailed in Division 01, Section 019113, General Commissioning Requirements, and apply to electrical systems.  The Subcontractor shall be familiar with all parts of Division 01, Section 019113, General Commissioning Requirements, and the commissioning plan issued by the Commissioning Authority and shall execute all commissioning responsibilities assigned to them in the Subcontract Documents.

        - The work of this Section shall be performed by a CTC (Certified Testing Company, Electrical), by the EC (Electrical Subcontractor), or the MSR (Manufacturer’s Service Representative).  The Commissioning Authority has some testing responsibilities for some equipment.  The specified checks and static tests are conducted by any of the above listed parties, but the tests requiring measurements or special tools or skills are generally conducted only by the CTC.  The “Check and Testing Responsibility Table”, included as Supplement 3 to Division 01, Section 019113, General Commissioning Requirements, provides specific allocation of checklist oversight and testing responsibilities.  The CTC, EC, and MSR shall document all checks and testing on check and test procedure forms submitted to and approved by the Commissioning Authority prior to testing.

        - The Subcontractor shall notify the University ahead of time when commissioning activities not yet performed or not yet scheduled will delay construction.  The Subcontractor shall be proactive in seeing that commissioning processes are executed and that the CA has the scheduling information needed to efficiently execute the commissioning process.

        - The Subcontractor shall respond to notices of issues identified during the commissioning process, making required corrections or clarifications and returning prompt notification to the Commissioning Authority according to the process given in Division 01, Section 019113, General Commissioning Requirements.

        - When completion of a task or other issue has been identified as holding up any commissioning process, particularly functional testing, the Subcontractor shall, within two (2) days of notification of the issue, notify the Commissioning Authority in writing providing an expected date of completion.  The Subcontractor shall notify the Commissioning Authority in writing within one day of completion.  It is not the responsibility of the Commissioning Authority to obtain this status information through meeting attendance, asking questions or field observation

        - Construction Checklists:  The Commissioning Authority or Subcontractor shall develop checklists as noted in the list of commissioned systems in Division 01, Section 019113, General Commissioning Requirements, following the process described in Division 01, Section 019113, General Commissioning Requirements, and in this Section.  At a minimum, for a given piece of equipment, checks from the inspection checklists in NETA Acceptance Testing Specifications for Electric Power Distribution Equipment and Systems shall be included in the electrical checklists.  The Subcontractor shall execute and document all checks.

        - Check and testing procedure and startup plan development and execution responsibilities are described in the “Check and Testing Responsibility Table”, Supplement 3 to Division 01, Section 019113, General Commissioning Requirements.

        - The Subcontractor shall review design documents, shop drawings and O&M manuals and manufacturer recommended installation and testing procedures of each system installation.

        - The Subcontractor shall monitor installation to ensure the equipment, configuration and quality of construction meets the design requirements, approved submittals and shop drawings.

        - The Subcontractor shall develop test procedures and forms and execute and document testing according to the requirements of this Section, Division 01, Section 019113, General Commissioning Requirements, and other specification sections containing testing requirements.

        - Tests of energized equipment shall be conducted when the equipment is operating at its normal capacity.  This may require some tests to be conducted after occupancy.

        - Training and Orientation:  The Subcontractor shall follow the facility staff orientation and training requirements as described in Division 01, Section 017900, Demonstration and Training, and other applicable technical sections.

        - Operation And Maintenance (O&M) Manuals:  Refer to Division 01, Section 019113, General Commissioning Requirements; and Division 01, Section 010000, General Requirements, for requirements for O&M manuals.

- equipment-specific verification and testing requirements

      - summary

        - This Part specifies the check and testing requirements for electrical components and systems.  From these requirements, the Commissioning Authority or Subcontractor shall develop detailed procedures and forms.  The general testing process, requirements and test method definitions are described in Division 01, Section 019113, General Commissioning Requirements.

      - checks and testS

        - Checks are intended to begin upon completion of a component or equipment installation.  Testing generally occurs later when systems are energized or nearing that point.  Beginning system testing before full completion does not relieve the Subcontractor from fully completing the system as soon as possible, including all construction checklists and may require retesting portions of the system once all components are fully functioning.

        - Refer to Division 01, Section 019113, General Commissioning Requirements, for specific details on non-conformance issues relating to construction checklists and tests.  Refer to Division 01, Section 019113, General Commissioning Requirements, for common requirements of deferred testing and to articles in this Section.

        - The check and test procedures and record forms shall contain the following:

          - The Subcontractors executing the checks or tests.

          - A list of the integral components being inspected and tested, equipment tag numbers, manufacturer, model number, pertinent performance information / rating data.

          - Test equipment used.

          - Construction checklists associated with the components, if any.

          - Any special required conditions of the check or test for each procedure.

          - Items, conditions or functions to be inspected, verified or tested, the checks and testing method given and a place provided with results recorded.

          - Acceptance criteria (or reference by specific table where the acceptance criteria is found).

          - For each procedure, list the technician performing check or test and company, witnesses of the tests and dates of tests.

          - Sampling strategies used.

        - The test procedures for dynamic equipment like lighting controls, emergency generator or fire alarm shall contain more step-by-step procedures with expected responses similar to the sample test provided as a supplement to Division 01, Section 019113, General Commissioning Requirements.  The test procedures and forms for more static components like panel boards, switch gear, circuit breakers, transformers, etc., can be more checklist-like in format.  For each piece of equipment, checks and test procedures and their documentation record forms may be different documents or combined in the same document, but checks and tests should be grouped.

        - At the Commissioning Authority's discretion, if large numbers or repeated deficiencies are encountered, the Subcontractor shall test and troubleshoot all remaining systems at issue on their own before commissioning with the Commissioning Authority will resume.

        - Sampling for Identical Units:  When there are a number of identical units, at the Commissioning Authority’s discretion, some or all procedures of a test for a piece of equipment or assembly may be omitted when these same tests on other pieces of identical equipment or assemblies were conducted without deficiency.

      - EQUIPMENT-SPECIFIC TESTING REQUIREMENTS

        - The following paragraphs define the testing requirements for each type of system or feature that is a part of the project.  The Commissioning Authority shall use this information to develop specific testing procedures for each of the systems to be commissioned.  The Subcontractor shall be responsible for support, execution and coordination of these tests as described in the project specifications including intersystem tests and interlocks with systems in Divisions other than Division 26.

        - The Commissioning Authority and Subcontractor shall coordinate with the project LEED coordinator to verify that LEED requirements for testing electrical systems are included in the tests.

        - Common Testing Requirements

          - The following requirements apply to all electrical systems and features that are to be commissioned when referenced below.  Tests shall:

            - Verify functionality and compliance with the design intent for each individual sequence module in the sequences of operation.  Verify proper operation of all control strategies, energy efficiency and self-diagnostics features by stepping through each sequence and documenting equipment and system performance.  Test every step in every written sequence and other significant modes, sequences and operational features not mentioned in written sequences; including startup, normal operation, shutdown, scheduled on and off, unoccupied and manual modes, safeties, alarms, over-rides, lockouts and power failure.

            - Verify all alarm and high and low limit functions and messages generated on all points with alarm settings.

            - Verify integrated performance of all components and control system components, including all interlocks and interactions with other equipment and systems.

            - Verify shut down and restart capabilities both for scheduled and unscheduled events (e.g., power failure recovery and normal scheduled start/stop).

            - When applicable, demonstrate a full cycle from off to on and no load to full load and then to no load and off.

            - Verify time of day schedules and setpoints.

            - Verify all energy saving control strategies.

            - Verify that monitoring system graphics are representative of the systems and that all points and control elements are in the same location on the graphic as they are in the field.

            - Verify operator control of all commandable control system points including proper security level access.

            - When testing procedures for commissioned equipment are listed in NETA Acceptance Testing Specifications for Electric Power Distribution Equipment and Systems the NETA test procedures shall be part of the testing requirements of this specification.  Additional testing procedures may be listed in this specification.

            - Common Acceptance Criteria

          - The following common acceptance criteria apply to all mechanical equipment, assemblies and features:

            - For the conditions, sequences and modes tested, the equipment, integral components and related equipment shall respond to varying loads and changing conditions and parameters appropriately as expected, according to the sequences of operation, as specified, according to acceptable operating practice and the manufacturer's performance specifications.  Verify that equipment operates within tolerances specified in:  governing codes, acceptance criteria contained in the construction documents, manufacturer's literature and according to good operating practice.

            - Systems shall accomplish their intended function and performance.

            - All safety trips shall require a manual reset to allow a system restart.

            - Resetting a manual safety shall result in a stable, safe, and predictable return to normal operation by the system.

            - Safety circuits and permissive control circuits shall function in all possible combinations of selector switch positions (hand, auto, inverter, bypass, etc.).

            - Other acceptance criteria are given in the equipment testing requirements articles or referenced standards.

            - Additional acceptance criteria shall be developed by the Commissioning Authority when detailed test procedures are developed.

            - When testing procedures for commissioned equipment are listed in NETA Acceptance Testing Specifications for Electric Power Distribution Equipment and Systems the NETA performance criteria shall apply.

        - Equipment-Specific Testing Requirements

          - Scheduled Lighting Controls

            - Apply the applicable common testing requirements and acceptance criteria.

            - Test Methods:  Utilize active testing, and trending when available.  If able to trend, trend all zones over a week period and follow the trending guidelines in Division 23, Section 230800, Commissioning of HVAC.

            - Sampling Strategy:  Manually test 20 percent of the zones or at least four.  If more than 10 percent or two zones fail, test another 10 percent sample.  If the second sample fails the Subcontractor shall document retesting on all zones on their own using a Commissioning Authority approved form.

          - Occupancy Sensor Lighting Controls

            - Apply applicable common testing requirements and acceptance criteria.  Test all unit functions, including sensor sensitivity and time-to-OFF functions and ensure that sensor location is proper and won't be tripped inadvertently by other occupants and movements outdoors, etc.

        - Test Methods

          - Utilize active test methods

            - Sampling Strategy:  Test 10 percent of the sensors or six, whichever is greater.  If more than 10 percent or two sensors fail, test another 10 percent sample.  If the second sample fails the Subcontractor shall document retesting on all units on their own using a Commissioning Authority approved form.

            - Additional Acceptance Criteria:  Reasonable sensitivity, no inadvertent trips, lights go off within 15 seconds of design.

          - Emergency Generator System

            - Apply applicable common testing requirements and acceptance criteria.

            - Test according to NETA 7.22.1 and NFPA 110 5.13 and per Division 01, Section 013500, Special Procedures.

            - Record all data and results.

            - Include the following tests:

              - When in enclosed spaces, verify combustion and ventilation air damper functions and pressure drop of exhaust.

              - Verify fuel oil system, diesel fuel storage tank, and level and low fuel indication alarms.

              - Verify all alarms, meters, and auxiliaries and interlocks to the BAS.

            - Building Test.  Under a cold generator condition, provide full utility power interruption under load and cause emergency power service operation.  Include all UPS in this test.  Load bank the UPS if necessary during test.

            - Verify all generator functions

            - Test auto-transfer switch operation under actual voltage drop, per Division 26, Section 263623, Automatic Transfer Switch With Bypass-Isolation Feature.

            - Using a power line disturbance monitor, measure the following times:  power failure to engine start command, engine start command to engine start (cranking time), engine start to point where generator is at proper volts and frequency and total time from power failure until ATS switches.

            - Verify system reporting & control monitoring point-to-point

            - Verify that each circuit and equipment served by emergency power, does power up.  Verify all functions of the Emergency Power Response Matrix.

            - Verify appropriate mechanical system and control system restart functions of all equipment served by the generator.

          - Step Load Tests

            - Test at 0 percent, 25 percent, 50 percent and 100 percent of full load.  Measure voltage and frequency and record all gaged engine conditions.  The test shall consist of running the engine-generator while connected to the resistive load bank for one hour, and then shutting down for 30 minutes.

            - Test for multiple generator starts.

            - Verify all operational data and start-up minimum time interval.

            - Verify 2-hour full load run full load bank (building load can serve as part of the load).

            - Verify all generator-running characteristics.

            - Verify battery-charging system.

          - Uninterruptible Power Supply

            - Apply applicable common testing requirements and acceptance criteria.

            - Test according to NETA 7.22.2 and NFPA 111-2001 5.6.

            - Test the UPS during the Integrated Building Test in the Emergency Generator System test requirements article in this Section.

          - Fire Alarm

            - Apply applicable common testing requirements and acceptance criteria.

            - Test the fire alarm and High Sensitivity Smoke Detection systems according to NFPA 110-1999 7-1 through 7-2, and Division 28, Section 283146.11, High Sensitivity Air Sampling Smoke Detection System; and Section 283110, MXL Fire Detection and Alarm System.

            - Document all test procedures and results.  A fire alarms system printout of the test annunciation record is not sufficient documentation.

            - Verify all fire alarm panel functions, alarms and troubles.

            - Verify all functions in the Fire Alarm Response Matrix, including remote communications.

            - Verify resetting of all equipment affected by an alarm.

            - Sampling Strategy.  Verify device functions and annunciations per using the approved sampling rate of the authority having jurisdiction and per LBNL.

END OF SECTION 260800