SECTION 262416 – panelboards

- GENERAL

      - SUMMARY

        - Related Documents:

          - Drawings and general provisions of the Subcontract apply to this Section.

          - Review these documents for coordination with additional requirements and information that apply to work under this Section.

        - Section Includes:

          - Provide the following panelboards:

            - Service entrance rated main distribution panelboards.

            - Distribution panelboards.

            - Lighting and appliance branch circuit panelboards.

            - Electronic Power Metering on panelboards per Section 2.05, when specified.

        - Related Sections:

          - Division 01 Section "General Requirements."

          - Division 01 Section "Special Procedures."

          - Division 01 Section "Lateral Force Procedures".

          - Division 26 Section "Common Work Results for Electrical".

          - Division 26 Section “Inspections and Testing for Electrical Work”.

          - Division 26 Section "600 Volt Conductors and Cable".

          - Division 26 Section "Secondary Grounding for Electrical Systems".

          - Division 26 Section "Electrical Conduit".

          - Division 26 Section “Electrical System Studies”.

      - REFERENCES

        - General:

          - The following documents form part of the Specifications to the extent stated. Where differences exist between codes and standards, the one affording the greatest protection shall apply.

          - Unless otherwise noted, the edition of the referenced code or standard that is current at the time of the “date of record” for the Work shall be considered the effective code or standard for the duration of the project.

          - Refer to Division 01 Section "General Requirements" for the list of applicable regulatory requirements.

          - Refer to specific Division 26 Sections for additional referenced codes and standards.

        - ANSI/NFPA 70 - National Electrical Code.

        - California Codes of Regulation, Title 24, Part 3.

        - Federal Specifications:

          - FS W-C-375 - Circuit Breakers, Molded Case, Branch Circuit and Service.

          - FS W-P-115 - Power Distribution Panel.

        - LBNL Construction Details and Design Guidelines; Vol. 3 Construction Details; Part VI Electrical Details

        - LBNL Electrical Authority having Jurisdiction: Standard Procedure for Safe Electrical Installations (IAHJ Program)

        - LBNL Electrical Safety Manual

        - LBNL Facilities Department Lateral Force Design Criteria.

        - LBNL Pub-3000 Chapter 8 - Electrical Safety Program

        - LBNL Pub-3000 Chapter 14 – Electrical Equipment Safety Program

        - LBNL Pub-3000 Chapter 18 - Lockout/Tagout Program

        - NFPA – National Fire Protection Association:

          - Standard for Electrical Safety in the Workplace (NFPA 70E)

        - NEMA – National Electrical Manufacturers Association:

          - NEMA AB 1 	Molded Case Circuit Breakers.

          - NEMA PB 1 	Panelboards.

          - NEMA PB 1.1 	Instructions for Safe Installation, Operation and Maintenance of Panelboards Rated 600 Volts or Less.

          - NEMA PB 1.2 	Application Guide for Ground-fault Protective Devices for Equipment.

        - NETA ATS - Acceptance Testing Specifications for Electrical Power Distribution Equipment and Systems

        - UL – Underwriters' Laboratories:

          - UL  67	Panelboards

          - UL  50	Enclosures for Electrical Equipment

- 3.	UL489	Molded Case Circuit breakers and Circuit Breaker Enclosures

      - SUBMITTALS

        - Submit under provisions of Division 01 Section "General Requirements" Paragraph 1.8.F, Submittals, and Division 01 Section "Special Procedures" Paragraph 1.7, Drawings and Specifications, Division 26 Section "Common Work Results for Electrical - Submittal" and as required by other sections of the Specifications."

        - Shop Drawings: The Subcontractor shall submit for approval Shop Drawings prepared in accordance with Division 01 Section "General Requirements", Paragraph1.8.F and as required by other sections of the Specifications.

        - All submittals and shop drawings shall be reviewed and approved by the Facilities Division Utility Group Electrical Engineer before procurement or fabrication of material and equipment.

        - Submit five (5) copies each submittal.

        - Shop Drawings for equipment and component devices.

        - Outline and support point dimensions, voltage, main bus ampacity, integrated short circuit ampere rating, circuit breaker arrangement, sizes and numbering system.

        - Product description and data sheets on circuit breakers, trip units, accessories, locking hardware, shunt trip, under-voltage release mechanism, typical thermal-magnetic or time-current curves for each size and type circuit breaker or trip unit.

        - The bidders shall list the exceptions taken from the specification with their quote. If no exceptions are listed with the bid, it is understood that the bidder shall meet the requirements of this specification and applicable Codes and Standards.

      - QUALITY ASSURANCE

        - Products shall be tested, approved and labeled/listed by Underwriters Laboratories, Inc., or by a nationally recognized testing laboratory (NRTL) as listed in Division 26 Specification "Common Work Results for Electrical."

        - Electrical equipment and materials shall be new and within one year of manufacture, complying with the latest codes and standards. No used, re-built, refurbished and/or re-manufactured electrical equipment and materials shall be furnished on this project.

      - COORDINATION

        - Refer to Division 01 Section "General Requirements" Paragraph 1.7.

        - Refer to Division 01 Section “Special Procedures” Paragraph 1.6 and Supplement for Equipment Energization Plan and Energization Validation and Authorization Package.

        - Refer to the LBNL Electrical Authority Having Jurisdiction: Standard Procedure for Safe Electrical Installations (IAHJ Program) in regards to the Facilities Energization Validation and Authorization Package (EVAP) process necessary before equipment energization.

      - DELIVERY, STORAGE, AND HANDLING

        - Store in a clean, dry space.  Maintain factory wrapping or provide an additional heavy canvas or heavy plastic cover to protect units from dirt, water, construction debris, and traffic.

        - Handle in accordance with manufacturer's written instructions. Lift only with lugs provided for the purpose.  Handle carefully to avoid damage to panelboard internal components, enclosure, and finish.

      - Warranty

        - Warranty period of one (1) year minimum shall start at the date the equipment is energized after acceptance by the University.

      - EXTRA MATERIALS

        - Keys:  Furnish two door keys for each panelboard to the University.

- PRODUCTS

      - MANUFACTURERS

        - Eaton/Cutler-Hammer.

        - General Electric.

        - Siemens.

      - BUS AND HARDWARE

        - Panelboards shall be completely factory assembled and equipped with a main circuit breaker and the type, size and number of branch circuit breakers, arranged and numbered as shown on the attached panel schedule(s). Panelboards shall be fully rated. Series rated panelboards are not acceptable.

        - All multi-pole breakers shall be common trip.  Branch circuits shall be arranged using double row construction. Bus sequence shall be ABC top to bottom, left to right for both top and bottom fed panels. Provisions or space for future breakers shall be located at the bottom of the panel and be fully bussed, complete with the necessary mounting hardware. Use at least 100 ampere breaker-connecting bus straps and mounting hardware.

        - Where SPARE is indicated on the panel schedule(s), the specified circuit breaker and 100 ampere (minimum) branch-circuit busing and mounting hardware shall be installed.

        - Where SPACE is indicated on the panel schedule(s), 100 ampere (minimum) branch-circuit busing and mounting hardware shall be installed, ready for future installation of circuit breakers, furnished by others. A minimum of 20 percent spare pole spaces, grouped in multiple of three, shall be provided in each panelboard, for future installation by the University. Provide single pole filler plates in the spaces, as required.

        - A nameplate shall be provided, and located near the top of the front trim on the exterior surface, listing panel type and ratings, as required by UL. Each circuit shall be permanently numbered to agree with the panel schedule, using plastic or metal buttons mounted adjacent to the breaker and secured by rivets or grommets with an engraved or depressed number.  Adhesive numbering tape, painted numbers, or use of more than one number per breaker is not acceptable.

        - Main vertical bus bars shall be copper and plated per UL requirements.  Bus bars shall be supported by glass-filled polyester-type insulators.  Bolts used to connect current-carrying parts together, shall be accessible for tightening from the front of the panel.  Bus bars shall be factory drilled and tapped with spacing arranged to permit breaker interchange, from the front, while the panel is energized.

        - Neutral bus shall be copper, 200 percent rated and insulated from the cabinet and other parts. It shall be rigidly mounted in the panel and shall be provided with a solderless cable connector for each circuit breaker and each space in the panelboard and the main connecting lug(s).

        - A copper equipment ground bus, of sufficient width and length, shall be solidly bolted and grounded to the enclosure at the bottom and shall leave clear space for the bottom cable entries.  The bus shall have sufficient termination points in number to agree with branch circuits and spaces. A solderless connector, for No. 2 to No. 4/0 cable size, shall be bolted to the ground bus.

        - Copper bus bars shall be of sufficient size to provide a current density of not more than 1000 amperes per square inch of cross section, and not more than 200 amperes per square inch at bolted connections.

        - Minimum Short Circuit Rating for Bus Bracing: The bus shall be braced for the minimum symmetrical short circuit rating of the panel, as shown on the panel schedule.

        - Provide main bus pressure connectors (main lugs) and separately supported sub-feed pressure connectors (lug landings) where noted. Provide additional bottom raceway space to accommodate pressure connectors and lug landings.  In no instance shall the gutter space be less than required by NFPA-70.

        - Pre-installed locking devices shall be provided for locking the main circuit breaker and each branch circuit breaker in the OPEN position, by means of a padlock.  Locking devices shall not be removable from the front of the panel with the trim in place.  Attachment of the locking device to the panel with adhesives is not acceptable.

      - CIRCUIT BREAKERS

        - Molded Case Circuit Breakers:  NEMA AB 1, FS W-C-375; Provide bolt-on type circuit breakers with integral thermal and instantaneous magnetic trip in each pole (common trip type). Provide circuit breakers, UL listed as Type HACR, for air conditioning equipment branch circuits. Provide circuit breakers, UL listed as Type SWD, for lighting circuits. Provide UL Class A ground fault interrupter circuit breakers where specified on panelboard schedules and/or the Drawings.]

        - Trip Unit:

          - Instantaneous magnetic trips shall be accessible and adjustable from the front of the breaker on frame size 100 amperes.

          - Trip units shall be interchangeable and adjustable for trip pick up and delay settings on frame size 225 amperes.

          - Breakers sized 400 amperes and higher shall be equipped with solid state trip units with long-time, short-time, instantaneous, and ground fault (LSIG) tripping characteristics.

        - Breakers shall be rigidly mounted, separately removable and independent of trim plates for their support.  Breakers shall be bolt on type.

        - Breakers shall be industrial grade with a minimum pole width of 1-inch (25.4 mm) and a minimum height of 5-1/2-inches (139.7 mm).  Miniature circuit breakers or breakers having a pole width of ½-inch are not acceptable.

        - The minimum symmetrical interrupting rating for molded-case circuit breakers shall be as specified on the panelboard schedule and/or Drawings. Series rated breakers are not acceptable.

      - CABINETS (BOXES)

        - All details of construction and methods of assembly shall meet the requirements of the "Enclosures for Electrical Equipment" of the Underwriters' Laboratories.  The panel box shall not be less than [20" (510 mm) wide] [___ inches wide], 4.5 inches (115 mm) deep and of sufficient height to enclose the specified main and branch circuit breakers, buses, metering equipment and wire gutter. The panelboard enclosure shall be fabricated from code-gauge galvanized or galvanized-annealed steel without knockouts and with full front flange.  The panel front shall be [surface] [flush], as indicated on the drawings and fabricated from cold rolled steel.  Surface mounted panel boxes shall be finished with an ANSI-61 light grey baked enamel.  There shall be no screws projecting into the wiring raceways. The panelboard enclosure type shall be [NEMA 1] [NEMA 3R] [as specified on the panelboard schedule].

        - The front trim shall have full-length hinged outer door designed to expose the wiring raceways and breakers, when open.  Another, inner hinged door shall expose breakers only, when open, making this a door-in-door construction.  Both doors shall open to the right.

        - Both doors shall be provided with concealed butt or piano hinges.  A suitable latch, which can be operated without tools, shall be provided to properly hold the inner door closed.  For doors 30 inches (765 mm) high or less, a flush-type latch is satisfactory.  For doors more than 30 inches (765 mm) high, a vault-type handle shall be provided with a three-point latch that holds the door closed at the top and bottom.  The outer door shall be secured with at least 4 captured oval head machine screws.

        - A sturdy metal frame, with a clear plastic cover, for an 8-1/2 by 11 inch (216 by 280 mm) panelboard schedule, shall be attached inside of the panel door with the RTV adhesive.

        - Panel trim and doors, and surface mounted cabinets shall be thoroughly cleaned, given a rust-inhibiting treatment, and finished with an ANSI-61 light grey baked enamel.

        - Panelboards shall bear the Underwriters' Laboratories label.

      - ELECTRONIC POWER METERING

        - The panelboard shall be provided with the electronic power metering, where shown on the Drawings and/or panelboard schedule.

        - An advanced digital electronic energy meter shall be used. The meter shall measure the real-time RMS values of the phase currents (Ampere), Ampere demand, phase and line voltages (Volts), KW, KW demand, KWHR, KVA, KVA demand, KVAR, KVAR demand, power factor, and frequency.

        - A communications module shall be provided using a 10Base-T Ethernet and industry standard RS-485 serial bus.

        - The advanced digital electronic energy meter shall have non-volatile memory to record at least 100 time-stamped alarms and events.

        - Potential, control power and current transformers, shorting terminal block, fuse blocks and fuses shall be completely installed and wired to the energy meter in the panelboard.

        - The electronic power meter shall be Square D PowerLogic ION7350 or higher, Siemens Model 9350 or higher, Power Measurement Limited Model 7350 or higher, no substitutions.

- EXECUTION

      - INSTALLATION

        - Install panelboards plumb [and flush with wall finishes], in conformance with NEMA PB 1.1.  Where surface mounted, provide suitable supports and rack branch circuit conduits.  Where mounted on concrete wall, install with 1/2 inches (15 mm) steel spacers behind the panel.  Mounting attachments and connections shall be designed in conformance with the minimum lateral seismic force of 0.5W per CBC.

        - Height: Install top of trim 78 inches (1980 mm) above finished floor, unless otherwise noted on drawings.

        - Provide filler plates for unused spaces in panelboards.

        - Provide typed [or neatly hand printed] 8-1/2 by11-inch (216 by 280 mm) circuit directory (panel schedule) for each panelboard, in the format as shown on the [panel schedules] [drawings].  Revise directory to reflect circuiting changes required to balance phase loads.

        - Stub [5] [__] empty 1 inch (25 mm) conduits to accessible location [above ceiling] [below floor] out of each recessed panelboard.

        - Labeling:  Refer to LBNL Construction Details and Design Guidelines; Vol. 3 Construction Details; Part VI Electrical Details – “INS126 – Electrical Panel Label” for the label layout to be used for panelboards and switchboards.  Refer to Division 26 Section – “Identifications for Electrical Services,” Part 3.3 – Labeling and Special Markings.

      - FIELD QUALITY CONTROL

        - Tests shall be made in the presence of an LBNL Inspector or the Electrical AHJ’s designated representative.  The application or interruption of power shall be programmed and directed in accordance with the approved EVAP, inclusive of the Equipment Energization Plan and necessary permits, work tasks and safety compliance steps.

        - Visual and Mechanical Inspection:  Verify panelboard enclosure type, trim and doors; correct frame size, type and layout of circuit breakers and required accessories are installed.  Inspect for physical damage, proper alignment, anchorage, and grounding.  Check proper installation and correctly torqued connections of circuit breakers and buswork.  Using a calibrated torque wrench, test and record values at all terminations.  Verify trip unit type, ratings and settings of overcurrent protective devices are in conformance with the approved Electrical System Studies for the project.

        - Test insulation of panelboard buses and circuit breakers (phase-to-phase and phase-to-ground) prior to applying power.  NETA approved tests forms shall be used for the certified test report(s).

        - The Subcontractor shall submit to the Project Manager five (5) copies of test results, certified in writing, witnessed, signed and dated, immediately upon completion of work for review and acceptance by the University.  An unsatisfactory condition revealed by these test results, or unsatisfactory methods of tests and/or testing apparatus and instruments, shall be bought to the attention of the Project Manager, Responsible Design Professional and the Facilities Division Utilities Group Electrical Engineer and/or the AHJ designated representative.  Corrections by the Subcontractor shall be validated by re-tests to the satisfaction of the Project Manager, the Registered Design Professional and the Facilities Division Utilities Group Electrical Engineer and/or the AHJ designated representative.

        - The Project Manager reserves the right to require that the Subcontractor perform and repeat tests that are deemed necessary to complete or check the tests or the certified records of the Subcontractor at any time during the course of the work.  The Subcontractor shall correct unsatisfactory portion of his work that is revealed by the tests or that may be due to progressive deterioration during this period, unless the item in question was a direct specification.

      - ACCEPTANCE AND ENERGIZATION

        - Final acceptance shall depend upon the satisfactory test results as performed in accordance with the manufacturer’s instructions.  After tests have been reviewed and approved by the University, energization may proceed in accordance with the approved Equipment Energization Plan and the Energization Validation and Authorization Package (EVAP).

        - Upon energization test and record readings for proper primary and secondary voltages, correct (clockwise) phase rotation and phase sequence (A-B-C).  Record readings and submit to University for review and acceptance approval.

        - Measure steady state load currents at each panelboard feeder.  Should the difference at panelboard between phases exceed 20 percent, rearrange circuits in the panelboard to balance the phase loads within 20 percent. Maintain proper phasing for multi-wire branch circuits.  Record readings and submit to University for review and acceptance approval.

      - FINAL SUBMITTALS

        - After completion of the installation, wiring and testing, the Subcontractor shall submit the following information to the University within two weeks of the equipment acceptance:

          - As-Built Panel Schedules.

          - Copy of the certified test report described in 3.2 above.

      - REFERENCE DRAWINGS AND PANELBOARD SCHEDULES

- Include drawings numbers for the panelboard schedules.  Schedules shall provide the following information:

        - Panelboard Number [    ]:

          - Panelboard type.

          - Number of phases.

          - Main bus ampacity.

          - Main circuit breaker trip rating.

          - Branch circuit breaker arrangement.

          - Branch circuit breaker trip sizes.

          - Flush or surface mounting.

          - Enclosure type.

          - Service entrance rating requirement (indicate `Y', if required).

          - Power Metering Requirement (indicate `Y', if required).

Circuit load.

END OF SECTION 262416