SECTION 263353 - Static Uninterruptible Power Supply

- GENERAL

      - SUMMARY

A.	Related Documents:

          - Drawings and general provisions of the Subcontract apply to this Section.

          - Review these documents for coordination with additional requirements and information that apply to work under this Section.

B.	Section Includes:

          - Three-phase, on-line, static type uninterruptible power supply (UPS) system complete with battery bank, battery circuit breaker and bypass/isolation switch.

C.	Related Sections:

          - Division 01 Section "General Requirements."

          - Division 01 Section "Special Procedures."

          - Division 26 Section "Common Work Results for Electrical".

          - Division 26 Section “Inspections and Testing for Electrical Work”.

          - Division 26 Section "600 Volt Conductors and Cable."

          - Division 26 Section "Secondary Grounding for Electrical Systems".

          - Division 26 Section "Electrical Conduit".

          - Division 26 Section "Boxes for Electrical Systems".

      - REFERENCES

A.	General:

          - The following documents form part of the Specifications to the extent stated. Where differences exist between codes and standards, the one affording the greatest protection shall apply.

          - Unless otherwise noted, the edition of the referenced code or standard that is current at the time of the “date of record” for the Work shall be considered the effective code or standard for the duration of the project.

          - Refer to Division 01 Section "General Requirements" for the list of applicable regulatory requirements.

          - Refer to specific Division 26 Sections for additional referenced codes and standards.

B.	ANSI/NFPA 70 - National Electrical Code.

C.	FCC rules and regulations of Part 15, Subpart J, Class A

D.	LBNL Construction Details and Design Guidelines; Vol. 3 Construction Details; Part VI Electrical Details

E.	LBNL Electrical Authority Having Jurisdiction: Standard Procedure for Safe Electrical Installations (IAHJ Program)

F.	LBNL Electrical Safety Manual

G.	LBNL Facilities Department Lateral Force Design Criteria.

H.	LBNL Pub-3000 Chapter 8 – Electrical Safety Program

I.	LBNL Pub-3000 Chapter 14 – Electrical Equipment Safety Program

J.	LBNL Pub-3000 Chapter 18 – Lockout/Tagout Program

K.	IEEE 587/ANSI C62.41 – Standards for Surge Withstand Ability

L.	UL 1778 – Standards for Uninterruptible Power Supply Equipment

      - SUBMITTALS

A.	Submit under provisions of Division 01 Section "General Requirements" Paragraph 1.8.F, Submittals, and Division 01 Section "Special Procedures" Paragraph 1.7, Drawings and Specifications, Division 26 Section "Common Work Results for Electrical - Submittals" and as required by other sections of the Specifications."

B.	Shop Drawings: The Subcontractor shall submit for approval Shop Drawings prepared in accordance with Division 01 Section "General Requirements", Paragraph 1.8.F and as required by other sections of the Specifications.

C.	All submittals and shop drawings shall be reviewed and approved by the Facilities Division Utility Group Electrical Engineer before procurement or fabrication of material and equipment.

D.	Submit shop drawings to show physical arrangements, connections, finishes, provisions for connections, access requirements for installation and maintenance, physical size, electrical characteristics and ratings, foundation and support details, and equipment weights, where such details are not indicated on the catalogue cuts.  The drawings and sketches shall be prepared in AutoCAD 2008.  Within twenty (20) days after the Award of Order, the vendor shall submit three (3) sets of complete shop drawings and product data along with the electronic drawing files on CD-ROM for University’s review and approval.  Provide specific data on the following:

          - Outline drawings showing overall assembly and drawings illustrating arrangement (plan, front, and side views) and lifting provisions.

          - Certified outline plan, general arrangement (setting plan), and anchor bolt details.  Drawings shall show the total weight and center of gravity of the assembled UPS system.

          - Arrangement, size, and location of electrical interface points and detailed elementary, schematic, wiring, and interconnection diagrams.

E.	Calculations prepared by a California registered Civil Engineer to demonstrate compliance with seismic requirements as set forth below, including bolting of the UPS to a [_______].  Anchorage of the system shall be designed for a minimum lateral seismic force of 0.5W. The dead load assumed to resist overturning shall not exceed 0.75W.

F.	Maintenance Manuals:

          - Maintenance Data:  Submit five (5) original copies and one (1) CD-ROM of recommended maintenance procedures and intervals.  Include spare parts data listing; source and current prices of replacement parts and supplies.

          - Furnish five (5) hardcopies and one (1) CD-ROM of as-built drawings which include the elementary and connection diagram.  Electronic drawing files shall be in AutoCAD 2008 format.

          - Furnish Time–Current curves of fuses, relays, circuit breaker trip units.  Time–Current curves shall be first generation originals on full size 11”x17” paper.

          - List special tools and spare parts required for maintenance and repair.

          - Name, address, and phone number of the service representative to be called in the event of equipment failure

G.	The bidders shall list the exceptions taken from the specification with their quote. If no exceptions are listed with the bid, it is understood that the bidder shall meet the requirements of this specification and applicable Codes and Standards.

      - QUALITY ASSURANCE

A.	Products shall be tested, approved and labeled/listed by Underwriters Laboratories, Inc., or by a nationally recognized testing laboratory (NRTL) as listed in Division 26 Specification "Common Work Results for Electrical."

B.	Electrical equipment and materials shall be new and within one year of manufacture, complying with the latest codes and standards. No used, re-built, refurbished and/or re-manufactured electrical equipment and materials shall be furnished on this project.

      - COORDINATION

A.	Refer to Division 01 Section "General Requirements" Paragraph 1.7.

B.	Refer to Division 01 Section “Special Procedures” Paragraph 1.6 and Supplement for Equipment Energization Plan and Energization Validation and Authorization Package.

C.	Refer to the LBNL Electrical Authority Having Jurisdiction: Standard Procedure for Safe Electrical Installations (IAHJ Program) in regards to the Facilities Energization Validation and Authorization Package (EVAP) process necessary before equipment energization.

      - DELIVERY, STORAGE, AND HANDLING

A.	Deliver materials to site in unopened crates, cartons or bundles as appropriate, clearly identified with manufacturer's name, Underwriter's Label, grade or identifying number.

B.	Store in a clean, dry space.  Maintain factory wrapping or provide an additional heavy canvas or heavy plastic cover to protect units from dirt, water, construction debris, and traffic.

C.	Handle in accordance with manufacturer's written instructions. Lift only with lugs provided for the purpose.  Handle carefully to avoid damage to transformer internal components, enclosure, and finish.

      - EXTRA MATERIALS

A.	As a separate quote, the bidders shall submit a recommended spare parts list with prices for one (1) year of operation.  The price list shall be valid for ninety (90) days from the date of the equipment delivery.

      - warranty

A.	Warranty: Warranty period shall start at the date the equipment is energized after acceptance by the University.  Submit five copies of the warranty certificate.

B.	The UPS system shall be warranted for a minimum of one (1) year from the date of commissioning against defects in material, equipment and workmanship.

- PRODUCTS

      - manufacturers

A.	MGE UPS Systems

B.	American Power Conversion Corporation (APC)

C.	Or equal

      - OPERATION CHARACTERISTICS

A.	Automatic system operating functions include the following:

          - Normal Conditions: Supply the load with power flowing from the normal AC power input terminals, through the rectifier/battery charger and inverter, with the battery connected in parallel with the rectifier output.

          - Abnormal Supply Conditions: When normal AC supply deviates from specified voltage, waveform or frequency limits, the battery supplies energy to maintain constant inverter output to the load.

          - When normal power fails, energy supplied by the battery through the inverter continues supply to the load without switching or disturbance.

          - When power is restored at the normal supply terminals of the system, the rectifier battery charger supplies power to the load through the inverter and simultaneously charges the battery.  Synchronize the inverter with the external source before transferring the load.

          - When the battery becomes discharged and normal supply is available charge the battery by the rectifier/battery charger.  On reaching full charge, shift the rectifier/battery charger to a float-charge mode.

          - When element of the UPS system fails and power is available at the normal supply terminals, the static bypass transfer switch switches the load to the normal source.

          - If a fault occurs in the system supplied by the UPS and current flows in excess of the overload rating of the UPS system, the static bypass transfer switch operates to bypass the fault current to the normal supply circuit of the UPS system for fault clearing.

          - When the fault has cleared, the static bypass transfer switch returns the load to the UPS system.

B.	Manual operating functions include the following:

          - Turning the inverter off causes the load to be transferred by the static bypass switch directly to the normal AC input source without interruption.

          - Turning the inverter on causes the static bypass switch to transfer the load to the inverter.

C.	Maintenance Bypass/Isolation Switch: Interlocked so the UPS cannot be operated unless the static bypass transfer switch is in the bypass mode.

          - Full isolation: the maintenance bypass system (MBS) shall provide complete electrical isolation of the UPS module for service without interrupting the connected load.  UPS AC supply input, static bypass transfer switch, and UPS load terminals are completely disconnected.

          - Maintenance Bypass: Load is supplied bypassing UPS.  UPS AC supply terminals are energized to permit operational checking, but system load terminals are isolated from the load.

          - Normal: UPS AC supply terminals are energized and the load is being supplied through either the static bypass transfer switch or the UPS rectifier and inverter.

      - SYSTEM CHARACTERISTICS

A.	The UPS capacity shall be [___] kVA/[___] kW.  Nominal input and output voltage shall be [480] [208] VAC, 3-phase, 3-wire plus ground

B.	Minimum duration of Supply: 15 [_____] minutes for a [___] kVA load being supplied solely from the battery.  Under steady-state or transient-load conditions the system shall remain within specified tolerances throughout the minimum duration when power is supplied from the battery

C.	Environmental Conditions:

          - Ambient Temperature: 0 to 40 degrees C (32 to 104 degrees F)

          - Relative Humidity: 0 to 95  percent, non-condensing

          - Altitude: Sea level to 1000 meters (3333 feet)

D.	Steady-state and transient output voltage remains within specified tolerances when steady-state AC input voltage varies +/-10 percent from normal voltage.

E.	Steady-state and transient output voltage remains within specified tolerances when steady-state input frequency varies +/-5 percent from normal and when the THD of the input voltage is 15 percent and the largest single harmonic component is a minimum of 5 percent of the fundamental value.

      - COMPATIBILITY WITH LOAD

A.	The system shall operate within specified tolerances, supply type of distribution system indicated and serve rated load comprised of a [_________________________________].

      - PERFORMANCE EFFICIENCIES

A.	Overall system efficiency when operated within indicated nominal input and output voltage and frequency limits: 90 percent at full load, 89 percent at ¾-load and 88 percent at ½-load.

B.	Maximum acoustical noise: 72 dB at one (1) meter from surface of the enclosure.

C.	Maximum energizing inrush: six (6) times the full-load current.

D.	Maximum output voltage regulation: for loads up to 50 percent unbalanced, +/-2 percent of full range battery voltage.

E.	Output frequency: 60 Hz, +/-0.5 percent of full range of input voltage, load, and battery voltage.

F.	Maximum harmonic content of output voltage waveform: 5 percent RMS total and 3 percent RMS for a single harmonic for rated full linear load more than the full range of battery condition and input voltage and frequency.

G.	Maximum harmonic content of output voltage waveform: 5 percent RMS total and 3 percent RMS for a single harmonic for rated full load with THD up to 80 percent of the full range of battery condition and input voltage and frequency.

H.	System overload capacity: at rated voltage, 110 percent of full-load rating for ten (10) minutes and 150 percent for 10 seconds.

I.	Maximum output voltage transient excursions from rated value: for the following instantaneous load changes, stated as percentages of rated full load, voltage shall remain within the stated percentages of rated value and recover to within +/-2 percent of that value within 100 ms:

          - 50 percent: +/8 percent

          - 100 percent: +/-10 percent

          - Loss of AC input power: +/-5 percent

          - Restoration of input power: +/-5 percent

      - GENERAL SYSTEM COMPONENTS

A.	Solid-state devices using hermetically sealed semiconductor elements include the rectifier/battery charger, inverter, static bypass transfer switch and system controls.

B.	Enclosure: Provide separate cabinets or compartments of enclosures for major components such as the static bypass transfer switch, rectifier, batteries, inverter and maintenance bypass switch.

C.	Control assemblies: Mount on modular plug-ins, arranged for easy maintenance.

D.	Surge Suppression: Protect UPS system input elements, rectifier/battery charger, inverter, controls and output components against voltage transients with surge suppressors listed in UL 1449 and tested according to IEEE C62.41, Category B.

E.	Power assemblies: Mount rectifier and inverter sections and static bypass transfer switch on modular plug-ins arranged for easy maintenance.

F.	Design and fabricate internal supports for assemblies, subassemblies, components, supports and fastenings for batteries to withstand static and anticipated seismic forces in accordance with LBNL Lateral Force Design Criteria.

      - RECTIFIER/BATTERY CHARGER

A.	The rectifier/battery charger shall have sufficient capacity to supply the inverter during full output load conditions and simultaneously recharge the battery from a fully discharged condition to 95 percent of full charge within ten (10) times the rated discharge time for duration of battery power at full load.

B.	Harmonic distortion shall be suppressed via harmonic filters or inherent in the rectifier/battery charger design to reduce the harmonic content of the current drawn from the input power source by the system to less than 10 percent for sources with X/R ratios from 2 to 30.  This applies for UPS load current from 0 to 100 percent of full load.

C.	Rectifier control circuits shall be made immune to frequency variations within the rated frequency range of the system.  Response time shall be field adjustable for compatibility with local generator-set power source.

D.	Battery float-charging conditions, in terms of voltage and charging current under normal operating conditions, shall be within the battery manufacturer’s written instructions for maximum battery life.

E.	The input power factor shall be at least 0.85 lagging when supply voltage and current are nominal rated values at UPS system rated full load.

      - BATTERY

A.	Batteries shall be sealed, maintenance free, valve regulated, recombinant, lead-calcium units, factory assembled in separate cabinets that match the UPS cabinet in appearance.  Equip the battery assembly with a battery disconnect switch.  Cabinets shall have provisions for draw-out removal of battery assembly to allow for inspection and testing.

      - BATTERY MONITORING SYSTEM

A.	Provide a battery ground fault detector that initiates an alarm when resistance to ground of the positive or negative bus of the battery is less than 5000 ohms.

B.	Provide, in the battery compartment, a smoke/high temperature detector that initiates an alarm when smoke is sensed or the temperature is greater than 75 degrees C within the compartment.

      - INVERTER

A.	The inverter shall be pulse-width modulated, with sinusoidal output.  Provide a bypass phase synchronization widow for compatibility with local generator-set power source.

      - STATIC BYPASS TRNASFER SWITCH

A.	The switch shall be rated for continuous duty at full load.  The switch shall provide make-before-break transfer in both directions.  Provide a contactor or electrically operated circuit breaker in the inverter output for electrical isolation.

      - MAINTENANCE BYPASS/ISOLATION SWITCH

A.	The switch shall be rated for continuous duty at rated full load of the system.

B.	Provide a key interlock that requires unlocking the maintenance bypass/isolation switch before switching from normal position with the key that is released only when the UPS is bypassed by the static bypass transfer switch.  The interlock shall be specifically designed for electrical component interlocking.

      - INDICATION AND CONTROL

A.	Group displays, indications and basic system controls shall be on a common control panel on the front of the UPS enclosure.

B.	Minimum displays, indicating devices and basic system controls include those listed below.  Provide sensors, transducers, terminals, relays and wiring required to support the listed items.  Provide visual and audible signals for alarm conditions.

C.	Indications shall be plain language messages on a liquid crystal or digital LED display.

          - Quantitative indications:

            - Input voltage, each phase, line-to-line.

            - Bypass input voltage, each phase, line-to-line.

            - Bypass input frequency.

            - Output voltage, each phase, line-to-line.

            - Output current each phase.

            - Output frequency.

            - DC bus voltage.

            - Elapsed time discharging battery

          - Status indications:

            - Normal operation.

            - Load on bypass.

            - Load on battery.

            - Inverter off.

            - Alarm condition exists.

          - Alarm indications:

            - Bypass AC input over voltage/under voltage.

            - Bypass AC input over frequency/under frequency.

            - Bypass AC input and inverter out of synchronization.

            - Bypass AC input wrong phase rotation.

            - Bypass AC input single-phase condition.

            - Bypass AC input filter fuse blown.

            - Internal frequency standard in use.

            - Battery system alarm

            - Control power failure.

            - Fan failure.

            - UPS overload.

            - Battery charging control faulty.

            - Input over voltage/under voltage.

            - Input circuit breaker tripped.

            - Input phase rotation wrong.

            - Input single-phase condition

            - Approaching end of battery operation.

            - Battery under voltage shutdown.

            - Maximum battery voltage.

            - Inverter fuse blown.

            - Inverter over temperature.

            - Static bypass transfer switch over temperature

            - Inverter power supply fault.

            - Inverter transistors out of saturation.

            - Identification of faulty inverter section/leg.

            - Inverter output over voltage/under voltage.

            - UPS overload shutdown.

            - Inverter current sensor fault.

            - Inverter output contactor open.

            - Inverter current limit

          - Controls:

            - Inverter on-off.

            - UPS start.

            - Battery test.

            - Alarm silence/test.

            - Output voltage adjustment.

D.	Provide Form c contacts for remote indication of the following conditions:

          - UPS on battery.

          - UPS on line.

          - UPS load on bypass.

          - UPS in alarm condition.

      - REMOTE UPS CONTROL AND MONITORING SYSTEM

A.	Provide a remote microprocessor for the unit control panel to indicate alarms and to control as specified in 2.14 above.  Record power line transients and provide analytical capability.  Include the items below, but do not include the remote computer or the connecting signal wiring.  System includes the following:

          - Modem and connectors for data transmission via an RS-232 link and external signal wiring to a computer.  External signal wiring and computer are not specified in this Section.

B.	Provide software for control and monitoring of UPS functions with on-screen explanations, interpretations and action guidance for monitored indications.  Include on-screen descriptions of control functions and instructions for their use.  Permit storage and analysis of power line transient records.  Software shall be IBM compatible.

      - ENCLOSURE

A.	The enclosure(s) shall be NEMA Type 1.  Ventilation shall be provided by redundant fans or blowers drawing in ambient air near the bottom of the enclosure and discharging near the top rear.

- EXECUTION

      - FACTORY TESTING

A.	Factory tests shall be performed on the complete UPS system, including battery, before shipment.  Include the following tests:

          - Functional test and demonstration of functions, controls, indicators, sensors and protective devices.

          - Full load test.

          - Transient load response test.

          - Overload test.

          - Power failure test.

          - Efficiency test at 50, 75 and 100 percent loads.

B.	Provide fourteen (14) days written notice of factory testing to allow the University’s representative to witness testing.

C.	Factory test results to include the following data:

          - Description of input source and output loads to be used.  Describe actions required to simulate source load variation and various operating conditions and malfunctions.

          - List of indications, parameter values and system responses considered satisfactory for each test action.  Include tabulation of actual observations during testing.

          - List if instruments and equipment required for duplication of factory tests in the field.

      - INSTALLATION

A.	Maintain minimum working clearance at equipment according to manufacturer’s written instructions.

B.	Install interconnections between system components.  Make connections to supply and load circuits according to manufacturer’s wiring diagrams, unless noted otherwise on the Drawings.

C.	Identify each battery cell individually.

D.	On completion of installation, inspect system components.  Remove paint splatters, other spots, dirt and debris.  Repair scratches and mars to finish to match original finish.  Clean components internally using methods and materials recommended by the manufacturer.

      - FIELD TESTING AND COMMISSIONING

        - Site Support, Inspection and Testing: The UPS manufacturer shall include in his bid the provision of assistance by the Technical Representative.  The assistance shall include, but not be limited to, supervision of unloading, setting, support, installation, and inspection of the UPS.  After inspection the Technical Representative shall test the equipment in accordance with an approved site test procedure.  Tests shall be made in the presence of an LBNL Inspector or the Electrical AHJ’s designated representative.  The application or interruption of power shall be programmed and directed in accordance with the approved EVAP, inclusive of the Equipment Energization Plan and necessary permits, work tasks and safety compliance steps.

        - The Vendor shall include in his bid three (3) working days of Technical Representative.  The Vendor shall also include in his bid the cost per day of such services if the services need to be extended or can be shortened.

        - The Subcontractor shall submit to the Project Manager five (5) copies of test results, certified in writing, witnessed, signed and dated, immediately upon completion of work for review and acceptance by the University.  An unsatisfactory condition revealed by these test results, or unsatisfactory methods of tests and/or testing apparatus and instruments, shall be bought to the attention of the Project Manager, Responsible Design Professional and the Facilities Division Utilities Group Electrical Engineer and/or the AHJ designated representative.  Corrections by the Subcontractor shall be validated by re-tests to the satisfaction of the Project Manager, the Registered Design Professional and the Facilities Division Utilities Group Electrical Engineer and/or the AHJ designated representative.

        - The Project Manager reserves the right to require that the Subcontractor perform and repeat tests that are deemed necessary to complete or check the tests or the certified records of the Subcontractor at any time during the course of the work.  The Subcontractor shall correct unsatisfactory portion of his work that is revealed by the tests or that may be due to progressive deterioration during this period, unless the item in question was a direct specification.

E.	A factory-authorized service representative shall pretest system functions, operations and protective devices and perform tests listed below.  Use instruments that have been calibrated according to NIST standards within six (6) months previous to field testing.

          - Load the system using a variable load bank simulating kVA, kW and power factor of loads for which the unit is rated.

          - Simulate malfunctions to verify protective device operation.

          - Test duration of supply on emergency, low battery voltage shutdown and transfers and restoration due to normal source failure.

          - Test harmonic content of input and output current less than 25, 50 and 100 percent of rated loads.

          - Test output voltage under specified transient load conditions.

          - Test remote status and alarm panel functions.

          - Test battery monitoring system functions.

F.	Correct deficiencies and retest until specified requirements are met.

G.	Equalize charging of battery cells according to manufacturer’s written instructions.  Record individual cell voltages.

      - ACCEPTANCE AND ENERGIZATION

        - Final acceptance shall depend upon the satisfactory test results as performed in accordance with the manufacturer’s instructions.  After tests have been reviewed and approved by the University, energization may proceed in accordance with the approved Equipment Energization Plan and the Energization Validation and Authorization Package (EVAP).

      - DEMONSTRATION AND TRAINING

A.	A factory-authorized service representative shall train University personnel on procedures and schedules related to startup and shutdown, troubleshooting, servicing and preventative maintenance.  Schedule training with the University with at least seven (7) days written notice.

      - FINAL SUBMITTALS

A.	After completion of the tests and adjustments listed above, the Subcontractor shall submit 5 sets of the following information to the University within two weeks after equipment acceptance date:

          - Complete as-built drawings.

          - Detailed catalog data on installed system components.

          - Operating and Shop Manuals

          - Field test reports.

          - Electronic file of the as-built drawings in AutoCAD 2008 on CD-ROM.  Only one (1) set required.

END OF SECTION 263353